## Sheet1
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | July 2025
System Name: | Weiss Estates Water |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 25 | 0.248 | 0.248
2 | 0 | 0 | 0 | 25 | 0.265 | 0.265
3 | 0 | 30 | -30 | 25 | 0.282 | 0.282
4 | 0 | 0 | 0 | 25 | 0.301 | 0.301
5 | 0 | 0 | 0 | 25 | 0.322 | 0.322
6 | 0 | 0 | 0 | 25 | 0.35 | 0.35
7 | 0 | 0 | 0 | 25 | 0.35 | 0.35
8 | 40 | 30 | 10 | 25 | 0.385 | 0.385
9 | 40 | 30 | 10 | 25 | 0.42 | 0.42
10 | 40 | 30 | 10 | 25 | 0.015 | 0.015
11 | 0 | 0 | 0 | 25 | 0.025 | 0.025
12 | 40 | 30 | 10 | 25 | 0.015 | 0.015
13 | 40 | 30 | 10 | 25 | 0.55 | 0.55
14 | 40 | 30 | 10 | 25 | 0.54 | 0.54
15 | 40 | 30 | 10 | 25 | 0.55 | 0.55
16 | 0 | 0 | 0 | 25 | 0.05 | 0.05
17 | 40 | 40 | 0 | 25 | 0.54 | 0.54
18 | 40 | 40 | 0 | 25 | 0.53 | 0.53
19 | 40 | 40 | 0 | 25 | 0.52 | 0.52
20 | 40 | 40 | 0 | 25 | 0.52 | 0.52
21 | 22 | 22 | 0 | 25 | 0.015 | 0.015
22 | 22 | 22 | 0 | 25 | 0.015 | 0.015
23 | 21 | 21 | 0 | 25 | 0.015 | 0.015
24 | 21 | 21 | 0 | 25 | 0.015 | 0.015
25 | 0 | 0 | 0 | 25 | 0.015 | 0.015
26 | 21 | 21 | 0 | 25 | 0.015 | 0.015
27 | 21 | 21 | 0 | 25 | 0.015 | 0.015
28 | 36 | 36 | 0 | 25 | 0.015 | 0.015
29 | 0 | 0 | 0 | 25 | 0.017 | 0.017
30 | 0 | 0 | 0 | 25 | 0.017 | 0.017
31 | 36 | 36 | 0 | 25 | 0.015 | 0.015
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 8/7/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )253-6191 |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.

## Sheet1 (2)
OHA – Drinking Water Services – Monthly UV Disinfection Report for Surface Water Systems Requiring 4-log Viral Inactivation | County | Coos | 2025-07-01
System Name: Weiss Estates Water System |  | PWS ID# | 41 -05581
Entry Point: Treatment Plant |  |  | Required Minimum Dose | 0.2 mg/l
Date | Time | Source(s) in use | Uninterrupted UV Operation? (i.e., No Alarms = Yes) | Notes
1 |  |  | Yes | 1.15
2 |  |  | Yes | 1.03
3 |  |  | Yes | 0.97
4 |  |  | Yes | 0.92
5 |  |  | Yes | 0.9
6 |  |  | Yes | 0.86
7 |  |  | Yes | 0.86
8 |  |  | Yes | 0.85
9 |  |  | Yes | 0.84
10 |  |  | Yes | 0.84
11 |  |  | Yes | 0.9
12 |  |  | Yes | 0.9
13 |  |  | Yes | 0.89
14 |  |  | yes | 0.86
15 |  | Fahy Lake | Yes | 0.83
16 |  |  | yes | 0.83
17 |  |  | yes | 0.81
18 |  |  | yes | 0.82
19 |  |  | yes | 0.83
20 |  |  | yes | 0.81
21 |  |  | yes | 0.75
22 |  |  | yes | 0.73
23 |  |  | yes | 0.71
24 |  |  | yes | 0.7
25 |  |  | yes | 0.7
26 |  |  | yes | 0.72
27 |  |  | yes | 0.69
28 |  |  | yes | 0.62
29 |  |  | yes | 0.51
30 |  |  | yes | 0.54
31 |  |  | yes | 0.5
If answered no above, what was the longest time period until UV operation was restored? hours If UV stopped working during water production, was DWS contacted? Yes No N/A Was a boil notice (Tier 1 Public Notice) issued, or is a Tier 2 public notice planned? Yes No N/A If not, please explain:
N/A Date & time UV reactor failed: Date & time it was returned to service: / / am/pm / / am/pm