## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Douglas
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021/Jul
System Name: | Little River Christian Camp |  |  | ID#: 41 | 4190476 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1
2
3
4
5
6
7
8 |  |  | 0.072 |  |  |  | 0.72
9 |  |  | 0.076 |  |  |  | 0.076
10 |  |  | 0.081 |  |  |  | 0.081
11
12 |  |  | 0.086 |  |  |  | 0.086
13
14 |  |  | 0.084 |  |  |  | 0.048
15 |  |  | 0.082 |  |  |  | 0.082
16 |  |  | 0.077 |  |  |  | 0.077
17 |  |  | 0.073 |  |  |  | 0.073
18
19
20
21
22 |  |  | 0.096 |  |  |  | 0.096
23 |  |  | 0.144 |  |  |  | 0.144
24 |  |  | 0.137 |  |  |  | 0.137
25
26
27
28
29 |  |  | 0.139 |  |  |  | 0.139
30 |  |  | 0.146 |  |  |  | 0.146
31 |  |  | 0.125 |  |  |  | 0.125
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Nolan Grant
SIGNATURE:
[5 empty] | PHONE #: ( 541 )496-3239 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Little River Christian Camp |  | ID#: 41 | 4190476 | Month/Year: | 2021/Jul | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 |  | 110
2 |  | 110
3 |  | 110
4 |  | 110
5 |  | 110
6 |  | 110
7 |  | 110
8 | 0.4 | 110 | 44 | 23.6 | 6.84 | 13.3486 | yes | 2.7
9 | 0.6 | 110 | 66 | 23.5 | 6.95 | 14.3515 | yes | 2.8
10 | 0.4 | 110 | 44 | 23.2 | 6.93 | 14.2018 | yes | 2.5
11 |  | 110
12 | 0.4 | 110 | 44 | 24.2 | 6.82 | 12.7088 | yes | 3.4
13 |  | 110
14 | 0.4 | 110 | 44 | 24.5 | 7.02 | 13.4407 | yes | 3.9
15 | 0.4 | 110 | 44 | 24.3 | 7.05 | 13.7845 | yes | 1.94
16 | 0.4 | 110 | 44 | 24.4 | 6.93 | 13.0749 | yes | 2.02
17 | 0.6 | 110 | 66 | 24.1 | 6.94 | 13.7188 | yes | 2.62
18 |  | 110
19 |  | 110
20 |  | 110
21 |  | 110
22 | 0.4 | 110 | 44 | 23.3 | 6.93 | 14.1045 | yes | 9.5
23 | 0.4 | 110 | 44 | 24.5 | 6.92 | 12.9352 | yes | 2.2
24 | 0.4 | 110 | 44 | 23.8 | 6.93 | 13.6274 | yes | 1.9
25 |  | 110
26 |  | 110
27 |  | 110
28 |  | 110
29 | 0.4 | 110 | 44 | 24.6 | 7.07 | 13.6063 | yes | 11
30 | 0.4 | 110 | 44 | 24.3 | 7.01 | 13.5752 | yes | 2.05
31 | 0.4 | 110 | 44 | 24.9 | 6.98 | 12.8757 | yes | 2.7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2