## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Douglas
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021/Jun
System Name: | Little River Christian Camp |  |  | ID#: 41 | 4190476 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.192 |  |  |  | 0.192
2 |  |  | 0.153 |  |  |  | 0.153
3 |  |  | 0.116 |  |  |  | 0.116
4
5
6
7
8
9 | [5 empty] | 0.117 | 0.117
10 | [5 empty] | 0.1 | 0.1
11 | [5 empty] | 0.115 | 0.115
12 | [5 empty] | 0.129 | 0.129
13 | [5 empty] | 0.123 | 0.123
14 | [5 empty] | 0.103 | 0.103
15 | [5 empty] | 0.127 | 0.127
16
17
18
19 | [5 empty] | 0.12 | 0.12
20 | [5 empty] | 0.162 | 0.162
21 | [5 empty] | 0.125 | 0.125
22 | [5 empty] | 0.125 | 0.125
23 | [5 empty] | 0.101 | 0.101
24 | [5 empty] | 0.107 | 0.107
25 | [5 empty] | 0.115 | 0.12
26 | [5 empty] | 0.12 | 0.12
27 | [5 empty] | 0.144 | 0.14
28
29
30
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Nolan Grant
SIGNATURE:
[5 empty] | PHONE #: ( 541 )496-3239 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Little River Christian Camp |  | ID#: 41 | 4190476 | Month/Year: | 2021/Jun | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.4 | 110 | 44 | 24.1 | 6.95 | 13.4511 | yes | 1.7
2 | 0.4 | 110 | 44 | 24.6 | 6.91 | 12.7969 | yes | 2.3
3 | 0.4 | 110 | 44 | 23.7 | 7.07 | 14.4752 | yes | 2.3
4 |  | 110
5 |  | 110
6 |  | 110
7 |  | 110
8 |  | 110
9 | 0.2 | 110 | 22 | 23.6 | 7.15 | 14.6781 | yes | 12.2
10 | 0.2 | 110 | 22 | 23.8 | 6.92 | 13.2594 | yes | 2.3
11 | 0.2 | 110 | 22 | 23.3 | 6.88 | 13.5159 | yes | 5.8
12 | 0.4 | 110 | 44 | 23.4 | 7.01 | 14.4422 | yes | 5.5
13 | 0.4 | 110 | 44 | 22.7 | 6.88 | 14.4204 | yes | 5
14 | 0.6 | 110 | 66 | 23.1 | 6.93 | 14.6391 | yes | 5.6
15 | 0.6 | 110 | 66 | 23.2 | 6.96 | 14.7062 | yes | 5.4
16 |  | 110
17 |  | 110
18 |  | 110
19 | 0.2 | 110 | 22 | 22.7 | 7.07 | 15.1439 | yes | 8.6
20 | 0.2 | 110 | 22 | 23.1 | 6.98 | 14.2372 | yes | 2.9
21 | 0.4 | 110 | 44 | 22.3 | 7.07 | 15.932 | yes | 4.6
22 | 0.4 | 110 | 44 | 22.5 | 6.95 | 15.0148 | yes | 4.7
23 | 0.4 | 110 | 44 | 21.1 | 7.06 | 17.2254 | yes | 6
24 | 0.4 | 110 | 44 | 18.4 | 6.99 | 20.15 | yes | 2.8
25 | 0.4 | 110 | 44 | 19.6 | 6.93 | 18.1613 | yes | 11.3
26 | 0.6 | 110 | 66 | 20.9 | 7.04 | 17.7374 | yes | 7.1
27 | 0.4 | 110 | 44 | 22.7 | 6.94 | 14.754 | yes | 3.4
28 |  | 110
29 |  | 110
30 |  | 110
31 |  | 110
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2