## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-02-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.05
3 |  |  | 0.05
4 |  |  | 0.06
5 |  |  | 0.05
6 |  |  | 0.05
7 |  |  | 0.05
8 |  |  | 0.05
9 |  |  | 0.05
10 |  |  | 0.05
11 |  |  | 0.06
12 |  |  | 0.05
13 |  |  | 0.05
14 |  |  | 0.05
15 |  |  | 0.05
16 |  |  | 0.05
17 |  |  | 0.05
18 |  |  | 0.05
19 |  |  | 0.07
20 |  |  | 0.09
21 |  |  | 0.07
22 |  |  | 0.06
23 |  |  | 0.07
24 |  |  | 0.07
25 |  |  | 0.06
26 |  |  | 0.06
27 |  |  | 0.07
28 |  |  | 0.07
29 |  |  | 0
30 |  |  | 0
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.83 | 161 | 133.63 | 13.4 | 7.6 | 37.118 | Yes | 30
2 | 0.95 | 161 | 152.95 | 13 | 7.3 | 34.5895 | Yes | 30
3 | 0.82 | 161 | 132.02 | 13 | 7.5 | 36.6951 | Yes | 30
4 | 0.92 | 161 | 148.12 | 13.4 | 7.5 | 36.1403 | Yes | 30
5 | 0.88 | 161 | 141.68 | 13 | 7.6 | 38.3339 | Yes | 30
6 | 0.76 | 161 | 122.36 | 14.3 | 7.9 | 38.7463 | Yes | 30
7 | 0.68 | 161 | 109.48 | 13.7 | 8 | 41.4548 | Yes | 30
8 | 0.6 | 161 | 96.6 | 12.9 | 7.8 | 40.2433 | Yes | 30
9 | 0.68 | 161 | 109.48 | 12.8 | 7.7 | 39.4013 | Yes | 30
10 | 0.63 | 161 | 101.43 | 13.1 | 7.4 | 34.3805 | Yes | 30
11 | 0.58 | 161 | 93.38 | 13.1 | 7.5 | 35.4723 | Yes | 30
12 | 0.54 | 161 | 86.94 | 12.7 | 7.6 | 37.6262 | Yes | 30
13 | 0.47 | 161 | 75.67 | 12.8 | 7.6 | 37.0816 | Yes | 30
14 | 0.53 | 161 | 85.33 | 12.3 | 7.3 | 35.015 | Yes | 30
15 | 0.46 | 161 | 74.06 | 12.8 | 7.8 | 39.8738 | Yes | 30
16 | 0.47 | 161 | 75.67 | 12.7 | 7.4 | 34.6717 | Yes | 30
17 | 0.52 | 161 | 83.72 | 12.1 | 7.2 | 34.2386 | Yes | 30
18 | 0.46 | 161 | 74.06 | 12.9 | 7.3 | 32.9339 | Yes | 30
19 | 0.53 | 161 | 85.33 | 12 | 7.4 | 36.9443 | Yes | 30
20 | 0.48 | 161 | 77.28 | 12.1 | 7.3 | 35.273 | Yes | 30
21 | 0.39 | 161 | 62.79 | 13.1 | 7.5 | 34.715 | Yes | 30
22 | 0.42 | 161 | 67.62 | 13.2 | 7.5 | 34.6026 | Yes | 30
23 | 0.48 | 161 | 77.28 | 12.5 | 7.5 | 36.4991 | Yes | 30
24 | 0.55 | 161 | 88.55 | 12.6 | 7.7 | 39.3438 | Yes | 30
25 | 0.5 | 161 | 80.5 | 12.9 | 7.4 | 34.3302 | Yes | 30
26 | 0.47 | 161 | 75.67 | 11.8 | 7.2 | 34.7118 | Yes | 30
27 | 0.54 | 161 | 86.94 | 12.5 | 7.7 | 39.5609 | Yes | 30
28 | 0.51 | 161 | 82.11 | 12.9 | 7.4 | 34.3692 | Yes | 30
29 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
30 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: