## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-05-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.1
2 |  |  | 0.07
3 |  |  | 0.07
4 |  |  | 0.07
5 |  |  | 0.07
6 |  |  | 0.08
7 |  |  | 0.08
8 |  |  | 0.3
9 |  |  | 0.07
10 |  |  | 0.09
11 |  |  | 0.08
12 |  |  | 0.32
13 |  |  | 0.09
14 |  |  | 0.07
15 |  |  | 0.08
16 |  |  | 0.08
17 |  |  | 0.07
18 |  |  | 0.11
19 |  |  | 0.07
20 |  |  | 0.1
21 |  |  | 0.08
22 |  |  | 0.08
23 |  |  | 0.07
24 |  |  | 0.08
25 |  |  | 0.1
26 |  |  | 0.1
27 |  |  | 0.1
28 |  |  | 0.08
29 |  |  | 0.08
30 |  |  | 0.08
31 |  |  | 0.09
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-05-21 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 161 | 101.43 | 15.5 | 7.3 | 28.229 | Yes | 30
2 | 0.51 | 161 | 82.11 | 15.6 | 7.5 | 29.7909 | Yes | 30
3 | 0.57 | 161 | 91.77 | 16 | 7.7 | 31.4523 | Yes | 30
4 | 0.5 | 161 | 80.5 | 16.1 | 7.8 | 32.1645 | Yes | 30
5 | 0.44 | 161 | 70.84 | 15.2 | 7.8 | 33.9193 | Yes | 30
6 | 0.61 | 161 | 98.21 | 15.4 | 7.6 | 31.69 | Yes | 30
7 | 0.61 | 161 | 98.21 | 15.3 | 7.6 | 31.902 | Yes | 30
8 | 0.66 | 161 | 106.26 | 15 | 7.5 | 31.5425 | Yes | 30
9 | 0.39 | 161 | 62.79 | 15.4 | 7.4 | 28.6962 | Yes | 30
10 | 0.48 | 161 | 77.28 | 15.2 | 7.6 | 31.6436 | Yes | 30
11 | 0.45 | 161 | 72.45 | 15 | 7.4 | 29.676 | Yes | 30
12 | 0.54 | 161 | 86.94 | 15.3 | 7.4 | 29.3874 | Yes | 30
13 | 0.6 | 161 | 96.6 | 15.5 | 7.6 | 31.4436 | Yes | 30
14 | 0.47 | 161 | 75.67 | 15.2 | 7.8 | 34.0352 | Yes | 30
15 | 0.51 | 161 | 82.11 | 15.5 | 7.8 | 33.5142 | Yes | 30
16 | 0.53 | 161 | 85.33 | 15.5 | 7.7 | 32.3706 | Yes | 30
17 | 0.5 | 161 | 80.5 | 15.5 | 8 | 36.0436 | Yes | 30
18 | 0.45 | 161 | 72.45 | 15.9 | 7.9 | 33.6325 | Yes | 30
19 | 0.48 | 161 | 77.28 | 15.1 | 7.8 | 34.3014 | Yes | 30
20 | 0.4 | 161 | 64.4 | 15.3 | 7.9 | 34.8043 | Yes | 30
21 | 0.49 | 161 | 78.89 | 15.4 | 7.8 | 33.6615 | Yes | 30
22 | 0.44 | 161 | 70.84 | 15.6 | 8 | 35.5617 | Yes | 30
23 | 0.4 | 161 | 64.4 | 15.9 | 7.8 | 32.2272 | Yes | 30
24 | 0.48 | 161 | 77.28 | 15.6 | 7.8 | 33.1784 | Yes | 30
25 | 0.56 | 161 | 90.16 | 15.6 | 7.7 | 32.2656 | Yes | 30
26 | 0.63 | 161 | 101.43 | 15.3 | 7.5 | 30.8121 | Yes | 30
27 | 0.69 | 161 | 111.09 | 15.5 | 7.5 | 30.6122 | Yes | 30
28 | 0.62 | 161 | 99.82 | 15.9 | 7.4 | 28.4913 | Yes | 30
29 | 0.54 | 161 | 86.94 | 15.8 | 7.7 | 31.7659 | Yes | 30
30 | 0.72 | 161 | 115.92 | 16 | 8 | 35.747 | Yes | 30
31 | 0.71 | 161 | 114.31 | 16.2 | 7.9 | 33.9565 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: