## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-07-21
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.22
2 |  |  | 0.26
3 |  |  | 0.28
4 |  |  | 0.26
5 |  |  | 0.15
6 |  |  | 0.22
7 |  |  | 0.12
8 |  |  | 0.22
9 |  |  | 0.14
10 |  |  | 0.3
11 |  |  | 0.22
12 |  |  | 0.14
13 |  |  | 0.17
14 |  |  | 0.44
15 |  |  | 0.2
16 |  |  | 0.13
17 |  |  | 0.16
18 |  |  | 0.17
19 |  |  | 0.15
20 |  |  | 0.17
21 |  |  | 0.14
22 |  |  | 0.17
23 |  |  | 0.14
24 |  |  | 0.14
25 |  |  | 0.26
26 |  |  | 0.35
27 |  |  | 0.38
28 |  |  | 0.37
29 |  |  | 0.4
30 |  |  | 0.42
31 |  |  | 0.44
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-07-21 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.69 | 161 | 111.09 | 19.1 | 7.6 | 24.9693 | Yes | 30
2 | 0.54 | 161 | 86.94 | 19.1 | 7.8 | 26.4422 | Yes | 30
3 | 0.64 | 161 | 103.04 | 19.3 | 7.9 | 27.3906 | Yes | 30
4 | 0.52 | 161 | 83.72 | 19.6 | 7.9 | 26.4798 | Yes | 30
5 | 0.54 | 161 | 86.94 | 19.6 | 7.7 | 24.635 | Yes | 30
6 | 0.39 | 161 | 62.79 | 19.7 | 7.4 | 21.5 | Yes | 30
7 | ..55 | 161 | #VALUE! | 19.9 | 7.4 | #VALUE! | Yes | 30
8 | 0.58 | 161 | 93.38 | 19.7 | 7.5 | 22.8134 | Yes | 30
9 | 0.62 | 161 | 99.82 | 19.5 | 7.6 | 24.1131 | Yes | 30
10 | 0.75 | 161 | 120.75 | 19.8 | 7.6 | 23.987 | Yes | 30
11 | 0.78 | 161 | 125.58 | 19.8 | 7.5 | 23.1874 | Yes | 30
12 | 0.68 | 161 | 109.48 | 19.9 | 7.7 | 24.5344 | Yes | 30
13 | 0.78 | 161 | 125.58 | 19.8 | 7.6 | 24.0697 | Yes | 30
14 | 0.8 | 161 | 128.8 | 19.9 | 7.6 | 23.9634 | Yes | 30
15 | 0.79 | 161 | 127.19 | 19.7 | 7.7 | 25.1816 | Yes | 30
16 | 0.82 | 161 | 132.02 | 19.9 | 7.9 | 26.8591 | Yes | 30
17 | 0.65 | 161 | 104.65 | 19.6 | 7.7 | 24.9476 | Yes | 30
18 | 0.88 | 161 | 141.68 | 19.7 | 7.7 | 25.4426 | Yes | 30
19 | 0.82 | 161 | 132.02 | 19.6 | 7.7 | 25.4384 | Yes | 30
20 | 0.94 | 161 | 151.34 | 20.1 | 7.6 | 24.0264 | Yes | 30
21 | 0.95 | 161 | 152.95 | 19.8 | 7.6 | 24.5438 | Yes | 30
22 | 0.94 | 161 | 151.34 | 19.7 | 7.4 | 22.9048 | Yes | 30
23 | 0.83 | 161 | 133.63 | 19.6 | 7.5 | 23.6368 | Yes | 30
24 | 0.87 | 161 | 140.07 | 19.6 | 7.2 | 21.2245 | Yes | 30
25 | 0.9 | 161 | 144.9 | 19.3 | 7.2 | 21.7335 | Yes | 30
26 | 0.72 | 161 | 115.92 | 19.4 | 7.2 | 21.1442 | Yes | 30
27 | 0.98 | 161 | 157.78 | 19.2 | 7.2 | 22.083 | Yes | 30
28 | 0.99 | 161 | 159.39 | 18.7 | 7.2 | 22.8657 | Yes | 30
29 | 0.88 | 161 | 141.68 | 19.1 | 7.4 | 23.6845 | Yes | 30
30 | 0.69 | 161 | 111.09 | 19.5 | 7.7 | 25.231 | Yes | 30
31 | 0.61 | 161 | 98.21 | 20.4 | 8.4 | 30.5344 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: