## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-08-21
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.45
2 |  |  | 0.46
3 |  |  | 0.44
4 |  |  | 0.45
5 |  |  | 0.44
6 |  |  | 0.64
7 |  |  | 0.55
8 |  |  | 0.95
9 |  |  | 0.66
10 |  |  | 0.45
11 |  |  | 0.52
12 |  |  | 0.89
13 |  |  | 0.6
14 |  |  | 0.84
15 |  |  | 0.71
16 |  |  | 0.52
17 |  |  | 0.46
18 |  |  | 0.47
19 |  |  | 0.43
20 |  |  | 0.37
21 |  |  | 0.37
22 |  |  | 0.22
23 |  |  | 0.39
24 |  |  | 0.42
25 |  |  | 0.54
26 |  |  | 0.46
27 |  |  | 0.39
28 |  |  | 0.34
29 |  |  | 0.27
30 |  |  | 0.48
31 |  |  | 0.76
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-08-21 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.53 | 161 | 85.33 | 19.5 | 7.7 | 24.7725 | Yes | 30
2 | 0.44 | 161 | 70.84 | 19.5 | 7.7 | 24.5182 | Yes | 30
3 | 0.61 | 161 | 98.21 | 19.4 | 7.6 | 24.2478 | Yes | 30
4 | 0.73 | 161 | 117.53 | 19.4 | 7.7 | 25.5176 | Yes | 30
5 | 0.63 | 161 | 101.43 | 20.1 | 8.1 | 27.9342 | Yes | 30
6 | 0.67 | 161 | 107.87 | 20.1 | 8.4 | 31.3653 | Yes | 30
7 | 0.51 | 161 | 82.11 | 20.1 | 8 | 26.5479 | Yes | 30
8 | 0.51 | 161 | 82.11 | 20 | 7.3 | 20.5761 | Yes | 30
9 | 0.42 | 161 | 67.62 | 19.8 | 7.3 | 20.6406 | Yes | 30
10 | 0.69 | 161 | 111.09 | 19.5 | 7.2 | 20.9294 | Yes | 30
11 | 0.78 | 161 | 125.58 | 19.7 | 7.2 | 20.8641 | Yes | 30
12 | 0.66 | 161 | 106.26 | 20.4 | 7.4 | 21.1561 | Yes | 30
13 | 0.84 | 161 | 135.24 | 20.2 | 7.2 | 20.311 | Yes | 30
14 | 0.5 | 161 | 80.5 | 20.1 | 8.8 | 35.6696 | Yes | 30
15 | 0.35 | 161 | 56.35 | 20.8 | 8.5 | 29.9517 | Yes | 30
16 | 0.25 | 161 | 40.25 | 20.6 | 7.5 | 20.6692 | Yes | 30
17 | 0.25 | 161 | 40.25 | 20.5 | 7.6 | 21.6042 | Yes | 30
18 | 0.72 | 161 | 115.92 | 19.7 | 7.2 | 20.7201 | Yes | 30
19 | 0.73 | 161 | 117.53 | 20.1 | 7.4 | 21.7635 | Yes | 30
20 | 1.3 | 161 | 209.3 | 19.6 | 7.7 | 26.8752 | Yes | 30
21 | 1.44 | 161 | 231.84 | 19.2 | 7.7 | 28.0497 | Yes | 30
22 | 1.31 | 161 | 210.91 | 19.3 | 8.4 | 35.5788 | Yes | 30
23 | 1.2 | 161 | 193.2 | 19.4 | 7.9 | 29.0051 | Yes | 30
24 | 0.81 | 161 | 130.41 | 18.4 | 7.4 | 24.6266 | Yes | 30
25 | 0.93 | 161 | 149.73 | 18.5 | 7.5 | 25.7424 | Yes | 30
26 | 0.78 | 161 | 125.58 | 19.4 | 7.2 | 21.291 | Yes | 30
27 | 0.74 | 161 | 119.14 | 18.9 | 7.6 | 25.4521 | Yes | 30
28 | 0.38 | 161 | 61.18 | 18.8 | 7.6 | 24.5877 | Yes | 30
29 | 0.48 | 161 | 77.28 | 19.5 | 7.6 | 23.7286 | Yes | 30
30 | 0.96 | 161 | 154.56 | 19 | 7.4 | 24.0642 | Yes | 30
31 | 1.08 | 161 | 173.88 | 19.4 | 7.5 | 24.6538 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: