## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-09-21
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.52
2 |  |  | 0.35
3 |  |  | 0.29
4 |  |  | 0.21
5 |  |  | 0.16
6 |  |  | 0.14
7 |  |  | 0.13
8 |  |  | 0.11
9 |  |  | 0.24
10 |  |  | 0.72
11 |  |  | 0.97
12 |  |  | 0.6
13 |  |  | 0.54
14 |  |  | 0.95
15 |  |  | 0.98
16 |  |  | 0.94
17 |  |  | 0.93
18 |  |  | 0.92
19 |  |  | 0.53
20 |  |  | 0.26
21 |  |  | 0.4
22 |  |  | 0.76
23 |  |  | 0.95
24 |  |  | 0.96
25 |  |  | 0.59
26 |  |  | 0.78
27 |  |  | 0.91
28 |  |  | 0.85
29 |  |  | 0.75
30 |  |  | 0.65
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-09-21 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.64 | 161 | 103.04 | 17.3 | 7.2 | 24.1335 | Yes | 30
2 | 0.66 | 161 | 106.26 | 17.5 | 7.2 | 23.866 | Yes | 30
3 | 0.95 | 161 | 152.95 | 18.2 | 7.4 | 25.3632 | Yes | 30
4 | 0.67 | 161 | 107.87 | 18.5 | 7.3 | 23.1895 | Yes | 30
5 | 0.49 | 161 | 78.89 | 19.9 | 7.2 | 19.9061 | Yes | 30
6 | 0.49 | 161 | 78.89 | 19.5 | 7.2 | 20.452 | Yes | 30
7 | 0.78 | 161 | 125.58 | 19.1 | 7.2 | 21.7263 | Yes | 30
8 | 0.84 | 161 | 135.24 | 19.5 | 7.4 | 22.9499 | Yes | 30
9 | 0.61 | 161 | 98.21 | 19.5 | 7.7 | 25.0008 | Yes | 30
10 | 0.68 | 161 | 109.48 | 19.7 | 7.2 | 20.6247 | Yes | 30
11 | 0.69 | 161 | 111.09 | 18.3 | 8 | 30.5651 | Yes | 30
12 | 0.69 | 161 | 111.09 | 18.8 | 7.3 | 22.7783 | Yes | 30
13 | 0.65 | 161 | 104.65 | 18.5 | 8.3 | 33.5499 | Yes | 30
14 | 0.64 | 161 | 103.04 | 18.1 | 7.2 | 22.8693 | Yes | 30
15 | 0.36 | 161 | 57.96 | 18.3 | 7.3 | 22.681 | Yes | 30
16 | 0.43 | 161 | 69.23 | 17.4 | 7.5 | 26.1707 | Yes | 30
17 | 0.33 | 161 | 53.13 | 18 | 7.8 | 27.788 | Yes | 30
18 | 0.25 | 161 | 40.25 | 17.9 | 7.7 | 26.7082 | Yes | 30
19 | 0.65 | 161 | 104.65 | 17.5 | 7.5 | 26.6587 | Yes | 30
20 | 0.28 | 161 | 45.08 | 17.7 | 7.6 | 26.1694 | Yes | 30
21 | 0.97 | 161 | 156.17 | 17.2 | 7.5 | 28.2127 | Yes | 30
22 | 0.93 | 161 | 149.73 | 17.9 | 7.4 | 25.8195 | Yes | 30
23 | 0.78 | 161 | 125.58 | 17.3 | 7.6 | 28.4608 | Yes | 30
24 | 0.55 | 161 | 88.55 | 17.7 | 7.6 | 26.9904 | Yes | 30
25 | 0.47 | 161 | 75.67 | 17.6 | 7.6 | 26.9243 | Yes | 30
26 | 0.55 | 161 | 88.55 | 18.1 | 7.8 | 28.3052 | Yes | 30
27 | 0.27 | 161 | 43.47 | 19.3 | 8.7 | 35.3199 | Yes | 30
28 | 0.56 | 161 | 90.16 | 17.4 | 7.9 | 30.8162 | Yes | 30
29 | 0.53 | 161 | 85.33 | 17.4 | 7.8 | 29.5932 | Yes | 30
30 | 0.52 | 161 | 83.72 | 17.7 | 7.9 | 30.0679 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: