## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-10-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.86
2 |  |  | 0.55
3 |  |  | 0.5
4 |  |  | 0.5
5 |  |  | 0.63
6 |  |  | 0.56
7 |  |  | 0.48
8 |  |  | 0.87
9 |  |  | 0.89
10 |  |  | 0.95
11 |  |  | 0.41
12 |  |  | 0.62
13 |  |  | 0.52
14 |  |  | 0.45
15 |  |  | 0.33
16 |  |  | 0.32
17 |  |  | 0.25
18 |  |  | 0.21
19 |  |  | 0.2
20 |  |  | 0.45
21 |  |  | 0.41
22 |  |  | 0.56
23 |  |  | 0.42
24 |  |  | 0.51
25 |  |  | 0.54
26 |  |  | 0.48
27 |  |  | 0.56
28 |  |  | 0.42
29 |  |  | 0.37
30 |  |  | 0.4
31 |  |  | 0.32
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.38 | 161 | 61.18 | 17.4 | 7.9 | 30.1905 | Yes | 30
2 | 0.6 | 161 | 96.6 | 17 | 7.9 | 31.7939 | Yes | 30
3 | 0.59 | 161 | 94.99 | 16.4 | 8 | 34.2982 | Yes | 30
4 | 0.62 | 161 | 99.82 | 16.8 | 8 | 33.5111 | Yes | 30
5 | 0.45 | 161 | 72.45 | 17.6 | 7.9 | 30.0287 | Yes | 30
6 | 0.64 | 161 | 103.04 | 16.7 | 8 | 33.8118 | Yes | 30
7 | 0.65 | 161 | 104.65 | 16.7 | 7.8 | 31.4355 | Yes | 30
8 | 0.76 | 161 | 122.36 | 16.5 | 7.9 | 33.4748 | Yes | 30
9 | 0.73 | 161 | 117.53 | 16.3 | 7.9 | 33.808 | Yes | 30
10 | 0.6 | 161 | 96.6 | 17 | 7.8 | 30.6377 | Yes | 30
11 | 0.77 | 161 | 123.97 | 14.3 | 7.8 | 37.386 | Yes | 30
12 | 0.9 | 161 | 144.9 | 14.1 | 7.8 | 38.4484 | Yes | 30
13 | 1.01 | 161 | 162.61 | 15 | 7.6 | 34.061 | Yes | 30
14 | 1.24 | 161 | 199.64 | 14.6 | 7.2 | 30.9678 | Yes | 30
15 | 1.35 | 161 | 217.35 | 14.5 | 7.4 | 33.9927 | Yes | 30
16 | 1.16 | 161 | 186.76 | 15.3 | 7.3 | 30.392 | Yes | 30
17 | 0.81 | 161 | 130.41 | 14.6 | 7.3 | 30.6003 | Yes | 30
18 | 0.67 | 161 | 107.87 | 15.1 | 7.9 | 36.3683 | Yes | 30
19 | 0.64 | 161 | 103.04 | 14.4 | 7.6 | 33.9888 | Yes | 30
20 | 0.63 | 161 | 101.43 | 15.6 | 7.4 | 29.1016 | Yes | 30
21 | 0.74 | 161 | 119.14 | 13.8 | 7.2 | 30.8567 | Yes | 30
22 | 0.69 | 161 | 111.09 | 15 | 7.6 | 32.8439 | Yes | 30
23 | 0.84 | 161 | 135.24 | 14 | 7.2 | 30.7966 | Yes | 30
24 | 0.66 | 161 | 106.26 | 14.9 | 7.8 | 35.4789 | Yes | 30
25 | 0.46 | 161 | 74.06 | 15 | 8.3 | 41.4286 | Yes | 30
26 | 0.67 | 161 | 107.87 | 13.9 | 7.3 | 31.5557 | Yes | 30
27 | 0.51 | 161 | 82.11 | 14.6 | 7.3 | 29.5713 | Yes | 30
28 | 0.83 | 161 | 133.63 | 14.7 | 7.4 | 31.616 | Yes | 30
29 | 0.79 | 161 | 127.19 | 14.6 | 7.2 | 29.4192 | Yes | 30
30 | 0.73 | 161 | 117.53 | 13.5 | 7.4 | 33.8599 | Yes | 30
31 | 0.72 | 161 | 115.92 | 15 | 7.3 | 29.4897 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: