## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-11-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.28
2 |  |  | 0.26
3 |  |  | 0.25
4 |  |  | 0.22
5 |  |  | 0.24
6 |  |  | 0.22
7 |  |  | 0.51
8 |  |  | 0.58
9 |  |  | 0.43
10 |  |  | 0.49
11 |  |  | 0.54
12 |  |  | 0.61
13 |  |  | 0.97
14 |  |  | 0.8
15 |  |  | 0.44
16 |  |  | 0.4
17 |  |  | 0.35
18 |  |  | 0.29
19 |  |  | 0.22
20 |  |  | 0.32
21 |  |  | 0.37
22 |  |  | 0.22
23 |  |  | 0.27
24 |  |  | 0.21
25 |  |  | 0.22
26 |  |  | 0.18
27 |  |  | 0.24
28 |  |  | 0.21
29 |  |  | 0.21
30 |  |  | 0.19
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2021-11-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 161 | 96.6 | 14.6 | 7.2 | 28.7882 | Yes | 30
2 | 0.67 | 161 | 107.87 | 14.7 | 7.7 | 34.6895 | Yes | 30
3 | 0.76 | 161 | 122.36 | 14.3 | 7.2 | 29.912 | Yes | 30
4 | 0.74 | 161 | 119.14 | 14.6 | 7.2 | 29.2518 | Yes | 30
5 | 0.51 | 161 | 82.11 | 13.2 | 7.2 | 31.2862 | Yes | 30
6 | 0.38 | 161 | 61.18 | 14.2 | 7.3 | 29.9249 | Yes | 30
7 | 0.72 | 161 | 115.92 | 13.9 | 7.2 | 30.5817 | Yes | 30
8 | 0.58 | 161 | 93.38 | 14.3 | 7.4 | 31.5593 | Yes | 30
9 | 0.58 | 161 | 93.38 | 13.9 | 7.5 | 33.6336 | Yes | 30
10 | 0.5 | 161 | 80.5 | 14.3 | 7.4 | 31.2731 | Yes | 30
11 | 0.37 | 161 | 59.57 | 15 | 7.6 | 31.6692 | Yes | 30
12 | 0.36 | 161 | 57.96 | 14.9 | 7.6 | 31.8448 | Yes | 30
13 | 0.42 | 161 | 67.62 | 14.8 | 7.4 | 29.9723 | Yes | 30
14 | 0.4 | 161 | 64.4 | 15 | 7.6 | 31.7776 | Yes | 30
15 | 0.41 | 161 | 66.01 | 15.1 | 7.5 | 30.453 | Yes | 30
16 | 0.66 | 161 | 106.26 | 15 | 7.4 | 30.3952 | Yes | 30
17 | 0.9 | 161 | 144.9 | 14.8 | 7.4 | 31.6572 | Yes | 30
18 | 1.06 | 161 | 170.66 | 15 | 7.65 | 34.8938 | Yes | 30
19 | 1.08 | 161 | 173.88 | 14.8 | 7.4 | 32.3126 | Yes | 30
20 | 0.98 | 161 | 157.78 | 15.5 | 7.3 | 29.3796 | Yes | 30
21 | 0.79 | 161 | 127.19 | 15 | 7.6 | 33.2196 | Yes | 30
22 | 0.3 | 161 | 48.3 | 14.8 | 7.7 | 33.04 | Yes | 30
23 | 0.72 | 161 | 115.92 | 15.1 | 7.7 | 33.9707 | Yes | 30
24 | 0.68 | 161 | 109.48 | 15.3 | 7.7 | 33.3693 | Yes | 30
25 | 0.59 | 161 | 94.99 | 15.1 | 7.8 | 34.7328 | Yes | 30
26 | 0.54 | 161 | 86.94 | 15.2 | 8.1 | 38.3245 | Yes | 30
27 | 0.48 | 161 | 77.28 | 15 | 7.8 | 34.5304 | Yes | 30
28 | 0.36 | 161 | 57.96 | 15.9 | 7.7 | 30.9144 | Yes | 30
29 | 0.31 | 161 | 49.91 | 14.9 | 7.3 | 28.3302 | Yes | 30
30 | 0.46 | 161 | 74.06 | 15.7 | 7.3 | 27.3179 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: