## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-07-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.09
2 |  |  | 0.102
3 |  |  | 0.11
4 |  |  | 0.09
5 |  |  | 0.09
6 |  |  | 0.09
7 |  |  | 0.1
8 |  |  | 0.1
9 |  |  | 0.1
10 |  |  | 0.12
11 |  |  | 0.1
12 |  |  | 0.09
13 |  |  | 0.1
14 |  |  | 0.09
15 |  |  | 0.12
16 |  |  | 0.11
17 |  |  | 0.12
18 |  |  | 0.11
19 |  |  | 0.09
20 |  |  | 0.1
21 |  |  | 0.12
22 |  |  | 0.13
23 |  |  | 0.11
24 |  |  | 0.13
25 |  |  | 0.1
26 |  |  | 0.12
27 |  |  | 0.11
28 |  |  | 0.11
29 |  |  | 0.11
30 |  |  | 0.12
31 |  |  | 0.15
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2022-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.11 | 161 | 178.71 | 18.3 | 7.8 | 29.7725 | Yes | 30
2 | 1.08 | 161 | 173.88 | 18.1 | 7.5 | 26.8996 | Yes | 30
3 | 0.94 | 161 | 151.34 | 17.9 | 7.4 | 25.8491 | Yes | 30
4 | 0.76 | 161 | 122.36 | 18.1 | 7.6 | 26.9157 | Yes | 30
5 | 0.67 | 161 | 107.87 | 18.4 | 7.6 | 26.1098 | Yes | 30
6 | 0.91 | 161 | 146.51 | 18.4 | 7.6 | 26.8367 | Yes | 30
7 | 0.97 | 161 | 156.17 | 18.4 | 7.5 | 26.0345 | Yes | 30
8 | 0.7 | 161 | 112.7 | 18.5 | 7.5 | 25.0729 | Yes | 30
9 | 0.73 | 161 | 117.53 | 18.5 | 7.6 | 26.1141 | Yes | 30
10 | 0.74 | 161 | 119.14 | 18.4 | 7.4 | 24.4297 | Yes | 30
11 | 0.66 | 161 | 106.26 | 18.5 | 7.5 | 24.9582 | Yes | 30
12 | 0.73 | 161 | 117.53 | 19.2 | 7.5 | 24.0039 | Yes | 30
13 | 0.67 | 161 | 107.87 | 19 | 7.4 | 23.2761 | Yes | 30
14 | 0.57 | 161 | 91.77 | 18.7 | 7.5 | 24.3724 | Yes | 30
15 | 0.58 | 161 | 93.38 | 18.9 | 7.5 | 24.0747 | Yes | 30
16 | 0.58 | 161 | 93.38 | 19.3 | 7.4 | 22.576 | Yes | 30
17 | 0.52 | 161 | 83.72 | 18.9 | 7.5 | 23.9095 | Yes | 30
18 | 0.5 | 161 | 80.5 | 18.9 | 7.4 | 22.9799 | Yes | 30
19 | 0.52 | 161 | 83.72 | 18 | 7.4 | 24.4696 | Yes | 30
20 | 0.48 | 161 | 77.28 | 19.4 | 7.5 | 23.0128 | Yes | 30
21 | 0.53 | 161 | 85.33 | 19.5 | 7.5 | 22.9901 | Yes | 30
22 | 0.48 | 161 | 77.28 | 19.7 | 7.5 | 22.5526 | Yes | 30
23 | 0.37 | 161 | 59.57 | 19.3 | 7.7 | 24.651 | Yes | 30
24 | 0.33 | 161 | 53.13 | 19.5 | 7.8 | 25.1307 | Yes | 30
25 | 0.35 | 161 | 56.35 | 19.7 | 7.6 | 23.0645 | Yes | 30
26 | 0.45 | 161 | 72.45 | 20 | 7.5 | 22.0251 | Yes | 30
27 | 0.32 | 161 | 51.52 | 20 | 7.5 | 21.6979 | Yes | 30
28 | 0.4 | 161 | 64.4 | 20.2 | 7.5 | 21.6053 | Yes | 30
29 | 0.43 | 161 | 69.23 | 21.2 | 7.5 | 20.2644 | Yes | 30
30 | 0.28 | 161 | 45.08 | 20.9 | 7.6 | 21.1017 | Yes | 30
31 | 0.44 | 161 | 70.84 | 21.2 | 7.6 | 21.0636 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: