## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-08-22
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.15
2 |  |  | 0.11
3 |  |  | 0.14
4 |  |  | 0.14
5 |  |  | 0.11
6 |  |  | 0.14
7 |  |  | 0.17
8 |  |  | 0.14
9 |  |  | 0.15
10 |  |  | 0.14
11 |  |  | 0.11
12 |  |  | 0.13
13 |  |  | 0.15
14 |  |  | 0.11
15 |  |  | 0.17
16 |  |  | 0.15
17 |  |  | 0.14
18 |  |  | 0.16
19 |  |  | 0.22
20 |  |  | 0.23
21 |  |  | 0.3
22 |  |  | 0.19
23 |  |  | 0.17
24 |  |  | 0.15
25 |  |  | 0.14
26 |  |  | 0.13
27 |  |  | 0.13
28 |  |  | 0.14
29 |  |  | 0.18
30 |  |  | 0.16
31 |  |  | 0.15
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2022-08-22 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.52 | 161 | 83.72 | 21.1 | 7.2 | 18.4151 | Yes | 30
2 | 0.53 | 161 | 85.33 | 21.1 | 7.5 | 20.6387 | Yes | 30
3 | 0.44 | 161 | 70.84 | 21.3 | 7.6 | 20.9218 | Yes | 30
4 | 0.45 | 161 | 72.45 | 21.2 | 7.9 | 23.5933 | Yes | 30
5 | 0.51 | 161 | 82.11 | 20 | 7.8 | 24.8079 | Yes | 30
6 | 0.65 | 161 | 104.65 | 20.3 | 7.9 | 25.6448 | Yes | 30
7 | 0.69 | 161 | 111.09 | 20.8 | 7.8 | 24.0004 | Yes | 30
8 | 0.68 | 161 | 109.48 | 21.2 | 7.6 | 21.6543 | Yes | 30
9 | 1.24 | 161 | 199.64 | 20.6 | 7.2 | 20.7033 | Yes | 30
10 | 0.95 | 161 | 152.95 | 21.3 | 7.5 | 21.3722 | Yes | 30
11 | 0.81 | 161 | 130.41 | 20.1 | 7.6 | 23.6705 | Yes | 30
12 | 0.91 | 161 | 146.51 | 20.1 | 7.7 | 24.854 | Yes | 30
13 | 0.84 | 161 | 135.24 | 19.8 | 7.6 | 24.236 | Yes | 30
14 | 0.69 | 161 | 111.09 | 19.4 | 7.8 | 26.3646 | Yes | 30
15 | 0.75 | 161 | 120.75 | 19.7 | 7.8 | 26.0179 | Yes | 30
16 | 0.78 | 161 | 125.58 | 19.9 | 7.5 | 23.0318 | Yes | 30
17 | 0.7 | 161 | 112.7 | 19.7 | 7.7 | 24.9232 | Yes | 30
18 | 0.63 | 161 | 101.43 | 20.9 | 7.7 | 22.8075 | Yes | 30
19 | 0.52 | 161 | 83.72 | 20.9 | 7.4 | 20.1255 | Yes | 30
20 | 0.43 | 161 | 69.23 | 20.6 | 7.6 | 21.9085 | Yes | 30
21 | 0.42 | 161 | 67.62 | 20.5 | 7.9 | 24.6446 | Yes | 30
22 | 0.39 | 161 | 62.79 | 20.1 | 7.6 | 22.5552 | Yes | 30
23 | 0.37 | 161 | 59.57 | 20.2 | 7.8 | 24.0869 | Yes | 30
24 | 0.39 | 161 | 62.79 | 20.3 | 7.7 | 23.1013 | Yes | 30
25 | 0.43 | 161 | 69.23 | 20.3 | 7.7 | 23.2078 | Yes | 30
26 | 0.34 | 161 | 54.74 | 20.8 | 7.6 | 21.392 | Yes | 30
27 | 0.43 | 161 | 69.23 | 20.2 | 8.4 | 30.3163 | Yes | 30
28 | 0.37 | 161 | 59.57 | 19.8 | 7.9 | 25.6824 | Yes | 30
29 | 0.59 | 161 | 94.99 | 19.6 | 7.7 | 24.7766 | Yes | 30
30 | 0.78 | 161 | 125.58 | 19.9 | 7.4 | 22.1863 | Yes | 30
31 | 0.6 | 161 | 96.6 | 20.1 | 7.6 | 23.1064 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: