## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-09-22
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.15
2 |  |  | 0.15
3 |  |  | 0.13
4 |  |  | 0.36
5 |  |  | 0.4
6 |  |  | 0.49
7 |  |  | 0.38
8 |  |  | 0.34
9 |  |  | 0.29
10 |  |  | 0.29
11 |  |  | 0.28
12 |  |  | 0.39
13 |  |  | 0.27
14 |  |  | 0.23
15 |  |  | 0.18
16 |  |  | 0.16
17 |  |  | 0.16
18 |  |  | 0.15
19 |  |  | 0.14
20 |  |  | 0.14
21 |  |  | 0.58
22 |  |  | 0.22
23 |  |  | 0.21
24 |  |  | 0.2
25 |  |  | 0.19
26 |  |  | 0.2
27 |  |  | 0.19
28 |  |  | 0.19
29 |  |  | 0.2
30 |  |  | 0.2
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2022-09-22 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 161 | 132.02 | 19.8 | 7.8 | 26.052 | Yes | 30
2 | 0.78 | 161 | 125.58 | 19.7 | 7.9 | 27.0971 | Yes | 30
3 | 0.87 | 161 | 140.07 | 20 | 7.5 | 23.1152 | Yes | 30
4 | 0.85 | 161 | 136.85 | 19.6 | 7.8 | 26.4943 | Yes | 30
5 | 0.79 | 161 | 127.19 | 19.1 | 7.8 | 27.2092 | Yes | 30
6 | 0.9 | 161 | 144.9 | 18.8 | 7.3 | 23.3347 | Yes | 30
7 | 0.89 | 161 | 143.29 | 19.2 | 7.4 | 23.5528 | Yes | 30
8 | 0.63 | 161 | 101.43 | 18.8 | 7.4 | 23.4832 | Yes | 30
9 | 0.74 | 161 | 119.14 | 18.1 | 7.6 | 26.8542 | Yes | 30
10 | 0.62 | 161 | 99.82 | 18.5 | 7.7 | 26.7652 | Yes | 30
11 | 0.48 | 161 | 77.28 | 19 | 8.2 | 30.6717 | Yes | 30
12 | 0.48 | 161 | 77.28 | 18.8 | 7.9 | 27.8094 | Yes | 30
13 | 0.53 | 161 | 85.33 | 18.7 | 7.7 | 26.1383 | Yes | 30
14 | 0.43 | 161 | 69.23 | 18.6 | 7.4 | 23.2607 | Yes | 30
15 | 0.45 | 161 | 72.45 | 18.2 | 7.2 | 22.2247 | Yes | 30
16 | 0.42 | 161 | 67.62 | 17.6 | 7.2 | 23.0614 | Yes | 30
17 | 0.42 | 161 | 67.62 | 17.6 | 7.3 | 23.9392 | Yes | 30
18 | 0.34 | 161 | 54.74 | 17.8 | 8.5 | 36.5349 | Yes | 30
19 | 0.55 | 161 | 88.55 | 17.6 | 8.3 | 35.2181 | Yes | 30
20 | 0.4 | 161 | 64.4 | 17.6 | 7.6 | 26.7095 | Yes | 30
21 | 0.71 | 161 | 114.31 | 17.2 | 7.3 | 25.4224 | Yes | 30
22 | 0.55 | 161 | 88.55 | 17.7 | 7.3 | 24.1362 | Yes | 30
23 | 0.26 | 161 | 41.86 | 18.2 | 7.6 | 25.2485 | Yes | 30
24 | 1.06 | 161 | 170.66 | 18.2 | 7.8 | 29.8016 | Yes | 30
25 | 0.98 | 161 | 157.78 | 18.9 | 8.3 | 33.9172 | Yes | 30
26 | 0.51 | 161 | 82.11 | 18.2 | 8.1 | 31.283 | Yes | 30
27 | 1.03 | 161 | 165.83 | 18.1 | 7.8 | 29.8988 | Yes | 30
28 | 0.83 | 161 | 133.63 | 18.2 | 7.8 | 29.0298 | Yes | 30
29 | 0.79 | 161 | 127.19 | 18.2 | 7.8 | 28.8976 | Yes | 30
30 | 0.64 | 161 | 103.04 | 18.2 | 7.8 | 28.407 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: