## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-10-22
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.2
2 |  |  | 0.21
3 |  |  | 0.22
4 |  |  | 0.24
5 |  |  | 0.25
6 |  |  | 0.28
7 |  |  | 0.29
8 |  |  | 0.33
9 |  |  | 0.35
10 |  |  | 0.38
11 |  |  | 0.76
12 |  |  | 0.82
13 |  |  | 0.75
14 |  |  | 0.75
15 |  |  | 0.69
16 |  |  | 0.86
17 |  |  | 0.86
18 |  |  | 0.82
19 |  |  | 0.78
20 |  |  | 0.67
21 |  |  | 0.81
22 |  |  | 0.66
23 |  |  | 0.71
24 |  |  | 0.61
25 |  |  | 0.78
26 |  |  | 0.74
27 |  |  | 0.63
28 |  |  | 0.67
29 |  |  | 0.73
30 |  |  | 0.5
31 |  |  | 0.74
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2022-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 161 | 99.82 | 18.1 | 7.9 | 29.6112 | Yes | 30
2 | 0.76 | 161 | 122.36 | 18.2 | 7.8 | 28.7988 | Yes | 30
3 | 0.65 | 161 | 104.65 | 18.1 | 7.8 | 28.6302 | Yes | 30
4 | 0.83 | 161 | 133.63 | 18.5 | 7.9 | 29.5294 | Yes | 30
5 | 0.27 | 161 | 43.47 | 18.6 | 7.9 | 27.5158 | Yes | 30
6 | 0.59 | 161 | 94.99 | 18.4 | 7.9 | 28.9244 | Yes | 30
7 | 0.83 | 161 | 133.63 | 18 | 8 | 31.6842 | Yes | 30
8 | 0.88 | 161 | 141.68 | 18.1 | 8 | 31.6533 | Yes | 30
9 | 0.59 | 161 | 94.99 | 18 | 8 | 30.8298 | Yes | 30
10 | 0.75 | 161 | 120.75 | 17.8 | 8 | 31.8184 | Yes | 30
11 | 0.75 | 161 | 120.75 | 18 | 8 | 31.3969 | Yes | 30
12 | 0.6 | 161 | 96.6 | 17.9 | 8 | 31.0716 | Yes | 30
13 | 0.96 | 161 | 154.56 | 17.2 | 8.1 | 35.1933 | Yes | 30
14 | 0.86 | 161 | 138.46 | 17.8 | 8 | 32.2193 | Yes | 30
15 | 0.78 | 161 | 125.58 | 18.2 | 8 | 31.0869 | Yes | 30
16 | 0.82 | 161 | 132.02 | 18.2 | 7.9 | 30.0926 | Yes | 30
17 | 0.4 | 161 | 64.4 | 18.1 | 8 | 29.9686 | Yes | 30
18 | 0.56 | 161 | 90.16 | 18.2 | 7.9 | 29.2134 | Yes | 30
19 | 0.75 | 161 | 120.75 | 17.8 | 8 | 31.8184 | Yes | 30
20 | 0.54 | 161 | 86.94 | 18.2 | 7.9 | 29.1468 | Yes | 30
21 | 0.7 | 161 | 112.7 | 17.8 | 8 | 31.6377 | Yes | 30
22 | 0.96 | 161 | 154.56 | 17 | 8 | 34.371 | Yes | 30
23 | 0.87 | 161 | 140.07 | 17.3 | 8 | 33.3485 | Yes | 30
24 | 0.65 | 161 | 104.65 | 17.7 | 8 | 31.6686 | Yes | 30
25 | 0.51 | 161 | 82.11 | 18.2 | 8 | 30.1449 | Yes | 30
26 | 0.97 | 161 | 156.17 | 14.7 | 7.9 | 38.64 | Yes | 30
27 | 0.79 | 161 | 127.19 | 16.8 | 8 | 34.165 | Yes | 30
28 | 1 | 161 | 161 | 15.9 | 8.1 | 38.5427 | Yes | 30
29 | 0.95 | 161 | 152.95 | 16.2 | 8.1 | 37.569 | Yes | 30
30 | 0.85 | 161 | 136.85 | 16.8 | 8 | 34.3988 | Yes | 30
31 | 0.76 | 161 | 122.36 | 16.6 | 8 | 34.505 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: