## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-12-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.57
2 |  |  | 0.28
3 |  |  | 0.33
4 |  |  | 0.65
5 |  |  | 0.38
6 |  |  | 0.28
7 |  |  | 0.31
8 |  |  | 0.37
9 |  |  | 0.57
10 |  |  | 0.39
11 |  |  | 0.37
12 |  |  | 0.59
13 |  |  | 0.4
14 |  |  | 0.35
15 |  |  | 0.35
16 |  |  | 0.46
17 |  |  | 0.43
18 |  |  | 0.38
19 |  |  | 0.36
20 |  |  | 0.48
21 |  |  | 0.46
22 |  |  | 0.31
23 |  |  | 0.4
24 |  |  | 0.44
25 |  |  | 0.46
26 |  |  | 0.4
27 |  |  | 0.45
28 |  |  | 0.47
29 |  |  | 0.4
30 |  |  | 0.34
31 |  |  | 0.5
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2022-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.61 | 161 | 98.21 | 13.4 | 8 | 41.9536 | Yes | 30
2 | 0.54 | 161 | 86.94 | 13.1 | 8.1 | 44.049 | Yes | 30
3 | 0.42 | 161 | 67.62 | 14.4 | 8 | 38.4256 | Yes | 30
4 | 0.54 | 161 | 86.94 | 13.2 | 8.1 | 43.7583 | Yes | 30
5 | 0.39 | 161 | 62.79 | 13.9 | 8.1 | 41.0723 | Yes | 30
6 | 0.74 | 161 | 119.14 | 12.5 | 8.1 | 46.8805 | Yes | 30
7 | 0.47 | 161 | 75.67 | 12 | 8.1 | 46.8598 | Yes | 30
8 | 0.42 | 161 | 67.62 | 14.5 | 8 | 38.1713 | Yes | 30
9 | 0.63 | 161 | 101.43 | 12.9 | 8 | 43.4646 | Yes | 30
10 | 0.34 | 161 | 54.74 | 13.4 | 8.1 | 42.2166 | Yes | 30
11 | 0.45 | 161 | 72.45 | 14 | 8.1 | 41.079 | Yes | 30
12 | 0.26 | 161 | 41.86 | 13.9 | 8 | 39.0083 | Yes | 30
13 | 0.26 | 161 | 41.86 | 14.6 | 8.1 | 38.6357 | Yes | 30
14 | 0.47 | 161 | 75.67 | 13.5 | 8 | 41.0213 | Yes | 30
15 | 0.41 | 161 | 66.01 | 12.7 | 8.1 | 44.5711 | Yes | 30
16 | 0.89 | 161 | 143.29 | 11.5 | 8.1 | 50.827 | Yes | 30
17 | 0.79 | 161 | 127.19 | 13 | 8 | 43.9661 | Yes | 30
18 | 0.75 | 161 | 120.75 | 13.3 | 8.1 | 44.5139 | Yes | 30
19 | 0.59 | 161 | 94.99 | 14.1 | 8 | 39.9606 | Yes | 30
20 | 0.96 | 161 | 154.56 | 12.4 | 8.1 | 48.2479 | Yes | 30
21 | 0.86 | 161 | 138.46 | 12.7 | 8.1 | 46.8958 | Yes | 30
22 | 0.86 | 161 | 138.46 | 11.7 | 8.1 | 49.9799 | Yes | 30
23 | 0.85 | 161 | 136.85 | 12 | 8.1 | 48.9332 | Yes | 30
24 | 0.85 | 161 | 136.85 | 12.6 | 8.1 | 47.1536 | Yes | 30
25 | 0.68 | 161 | 109.48 | 12.9 | 8 | 43.7111 | Yes | 30
26 | 0.71 | 161 | 114.31 | 14.2 | 8.1 | 41.7488 | Yes | 30
27 | 0.76 | 161 | 122.36 | 13.7 | 8.1 | 43.3996 | Yes | 30
28 | 0.6 | 161 | 96.6 | 13.4 | 8 | 41.9061 | Yes | 30
29 | 0.88 | 161 | 141.68 | 13.3 | 8 | 43.5422 | Yes | 30
30 | 0.83 | 161 | 133.63 | 13.3 | 8 | 43.2967 | Yes | 30
31 | 0.75 | 161 | 120.75 | 13.7 | 8.1 | 43.3505 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: