## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-01-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.4
2 |  |  | 0.36
3 |  |  | 0.37
4 |  |  | 0.46
5 |  |  | 0.46
6 |  |  | 0.43
7 |  |  | 0.39
8 |  |  | 0.45
9 |  |  | 0.4
10 |  |  | 0.41
11 |  |  | 0.41
12 |  |  | 0.36
13 |  |  | 0.39
14 |  |  | 0.47
15 |  |  | 0.45
16 |  |  | 0.35
17 |  |  | 0.53
18 |  |  | 0.49
19 |  |  | 0.39
20 |  |  | 0.34
21 |  |  | 0.33
22 |  |  | 0.38
23 |  |  | 0.43
24 |  |  | 0.42
25 |  |  | 0.31
26 |  |  | 0.36
27 |  |  | 0.29
28 |  |  | 0.25
29 |  |  | 0.29
30 |  |  | 0.3
31 |  |  | 0.48
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.73 | 161 | 117.53 | 13.1 | 8.1 | 45.0052 | Yes | 30
2 | 0.71 | 161 | 114.31 | 13 | 8.1 | 45.2018 | Yes | 30
3 | 0.3 | 161 | 48.3 | 14 | 8.1 | 40.3873 | Yes | 30
4 | 0.76 | 161 | 122.36 | 11.9 | 8.2 | 50.5229 | Yes | 30
5 | 0.7 | 161 | 112.7 | 12.4 | 8.1 | 46.8406 | Yes | 30
6 | 0.3 | 161 | 48.3 | 14.6 | 8.1 | 38.8113 | Yes | 30
7 | 0.82 | 161 | 132.02 | 12.2 | 8.2 | 49.8612 | Yes | 30
8 | 0.71 | 161 | 114.31 | 13.3 | 8.1 | 44.3131 | Yes | 30
9 | 0.6 | 161 | 96.6 | 13.5 | 8.1 | 43.1896 | Yes | 30
10 | 0.73 | 161 | 117.53 | 12.3 | 8.1 | 47.314 | Yes | 30
11 | 0.7 | 161 | 112.7 | 13.8 | 8.1 | 42.8215 | Yes | 30
12 | 0.88 | 161 | 141.68 | 12.7 | 8.1 | 47.0018 | Yes | 30
13 | 0.96 | 161 | 154.56 | 12.9 | 8.1 | 46.8052 | Yes | 30
14 | 0.87 | 161 | 140.07 | 12.8 | 8.1 | 46.6393 | Yes | 30
15 | 0.82 | 161 | 132.02 | 13.3 | 8.1 | 44.8675 | Yes | 30
16 | 0.66 | 161 | 106.26 | 13.9 | 8.1 | 42.3467 | Yes | 30
17 | 0.57 | 161 | 91.77 | 13.5 | 8.1 | 43.0433 | Yes | 30
18 | 0.65 | 161 | 104.65 | 13.3 | 8.1 | 44.0136 | Yes | 30
19 | 0.57 | 161 | 91.77 | 12.5 | 8.1 | 45.9889 | Yes | 30
20 | 0.62 | 161 | 99.82 | 12.7 | 8.1 | 45.6415 | Yes | 30
21 | 0.61 | 161 | 98.21 | 12.5 | 8.1 | 46.1972 | Yes | 30
22 | 0.67 | 161 | 107.87 | 12.4 | 8 | 45.0618 | Yes | 30
23 | 0.51 | 161 | 82.11 | 13.2 | 8.1 | 43.6101 | Yes | 30
24 | 0.3 | 161 | 48.3 | 13.7 | 8.1 | 41.1986 | Yes | 30
25 | 0.81 | 161 | 130.41 | 11.3 | 8.1 | 51.0418 | Yes | 30
26 | 0.82 | 161 | 132.02 | 11.8 | 8.1 | 49.4208 | Yes | 30
27 | 0.87 | 161 | 140.07 | 11.7 | 8.1 | 50.0371 | Yes | 30
28 | 0.73 | 161 | 117.53 | 11.8 | 8.1 | 48.9153 | Yes | 30
29 | 0.65 | 161 | 104.65 | 12 | 8.1 | 47.8296 | Yes | 30
30 | 0.45 | 161 | 72.45 | 11.6 | 8.1 | 48.0131 | Yes | 30
31 | 0.83 | 161 | 133.63 | 9.6 | 8 | 55.3319 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: