## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-04-23
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.05
3 |  |  | 0.05
4 |  |  | 0.058
5 |  |  | 0.059
6 |  |  | 0.056
7 |  |  | 0.054
8 |  |  | 0.049
9 |  |  | 0.05
10 |  |  | 0.051
11 |  |  | 0.047
12 |  |  | 0.047
13 |  |  | 0.048
14 |  |  | 0.049
15 |  |  | 0.05
16 |  |  | 0.051
17 |  |  | 0.045
18 |  |  | 0.047
19 |  |  | 0.048
20 |  |  | 0.048
21 |  |  | 0.049
22 |  |  | 0.048
23 |  |  | 0.049
24 |  |  | 0.05
25 |  |  | 0.051
26 |  |  | 0.05
27 |  |  | 0.052
28 |  |  | 0.051
29 |  |  | 0.061
30 |  |  | 0.06
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-04-23 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 161 | 101.43 | 13.8 | 7.7 | 36.6617 | Yes | 30
2 | 0.63 | 161 | 101.43 | 13.8 | 7.6 | 35.3329 | Yes | 30
3 | 0.68 | 161 | 109.48 | 13 | 7.4 | 34.8072 | Yes | 30
4 | 0.63 | 161 | 101.43 | 13.1 | 7.5 | 35.6743 | Yes | 30
5 | 0.69 | 161 | 111.09 | 12.8 | 7.4 | 35.3134 | Yes | 30
6 | 0.64 | 161 | 103.04 | 13.3 | 7.3 | 32.7313 | Yes | 30
7 | 0.67 | 161 | 107.87 | 13.3 | 7.4 | 34.0805 | Yes | 30
8 | 0.6 | 161 | 96.6 | 13.4 | 7.6 | 36.1618 | Yes | 30
9 | 0.55 | 161 | 88.55 | 13.7 | 7.6 | 35.247 | Yes | 30
10 | 0.43 | 161 | 69.23 | 14.4 | 7.5 | 31.9813 | Yes | 30
11 | 0.56 | 161 | 90.16 | 13.2 | 7.7 | 37.8506 | Yes | 30
12 | 0.53 | 161 | 85.33 | 13.8 | 7.3 | 31.2644 | Yes | 30
13 | 0.61 | 161 | 98.21 | 13 | 7.3 | 33.2782 | Yes | 30
14 | 0.61 | 161 | 98.21 | 13.2 | 7.3 | 32.8378 | Yes | 30
15 | 0.63 | 161 | 101.43 | 14.4 | 7.6 | 33.9502 | Yes | 30
16 | 0.53 | 161 | 85.33 | 14.8 | 7.9 | 36.5158 | Yes | 30
17 | 0.6 | 161 | 96.6 | 13.3 | 7.6 | 36.4029 | Yes | 30
18 | 0.73 | 161 | 117.53 | 13 | 7.9 | 42.0915 | Yes | 30
19 | 0.75 | 161 | 120.75 | 12.8 | 7.4 | 35.5548 | Yes | 30
20 | 0.59 | 161 | 94.99 | 13.7 | 7.4 | 32.8843 | Yes | 30
21 | 0.69 | 161 | 111.09 | 13.1 | 7.4 | 34.6157 | Yes | 30
22 | 0.8 | 161 | 128.8 | 14.3 | 7.4 | 32.3596 | Yes | 30
23 | 0.73 | 161 | 117.53 | 14.1 | 7.5 | 33.7595 | Yes | 30
24 | 0.71 | 161 | 114.31 | 13.9 | 7.5 | 34.1343 | Yes | 30
25 | 0.75 | 161 | 120.75 | 13.2 | 7.4 | 34.6214 | Yes | 30
26 | 0.67 | 161 | 107.87 | 14.9 | 7.3 | 29.5185 | Yes | 30
27 | 0.74 | 161 | 119.14 | 13.7 | 7.4 | 33.4501 | Yes | 30
28 | 0.57 | 161 | 91.77 | 14.5 | 7.6 | 33.4957 | Yes | 30
29 | 0.55 | 161 | 88.55 | 14.7 | 7.7 | 34.2197 | Yes | 30
30 | 0.53 | 161 | 85.33 | 16.4 | 7.3 | 26.2762 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: