## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-05-23
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.06
2 |  |  | 0.059
3 |  |  | 0.064
4 |  |  | 0.063
5 |  |  | 0.063
6 |  |  | 0.067
7 |  |  | 0.067
8 |  |  | 0.066
9 |  |  | 0.067
10 |  |  | 0.064
11 |  |  | 0.065
12 |  |  | 0.067
13 |  |  | 0.069
14 |  |  | 0.07
15 |  |  | 0.072
16 |  |  | 0.072
17 |  |  | 0.074
18 |  |  | 0.076
19 |  |  | 0.076
20 |  |  | 0.081
21 |  |  | 0.077
22 |  |  | 0.077
23 |  |  | 0.073
24 |  |  | 0.078
25 |  |  | 0.074
26 |  |  | 0.076
27 |  |  | 0.078
28 |  |  | 0.077
29 |  |  | 0.076
30 |  |  | 0.089
31 |  |  | 0.08
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-05-23 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 161 | 99.82 | 15.3 | 7.7 | 33.1424 | Yes | 30
2 | 0.65 | 161 | 104.65 | 15.2 | 7.5 | 31.0891 | Yes | 30
3 | 0.78 | 161 | 125.58 | 15.5 | 7.4 | 29.8022 | Yes | 30
4 | 0.75 | 161 | 120.75 | 15.8 | 7.3 | 28.05 | Yes | 30
5 | 0.68 | 161 | 109.48 | 15.4 | 7.3 | 28.5811 | Yes | 30
6 | 0.66 | 161 | 106.26 | 16.4 | 7.4 | 27.6803 | Yes | 30
7 | 0.64 | 161 | 103.04 | 17 | 7.5 | 27.5348 | Yes | 30
8 | 0.49 | 161 | 78.89 | 16.2 | 7.7 | 30.7539 | Yes | 30
9 | 0.61 | 161 | 98.21 | 15.9 | 7.9 | 34.2498 | Yes | 30
10 | 0.58 | 161 | 93.38 | 16.4 | 7.7 | 30.6591 | Yes | 30
11 | 0.66 | 161 | 106.26 | 16.1 | 7.7 | 31.5651 | Yes | 30
12 | 0.65 | 161 | 104.65 | 15.3 | 7.6 | 32.0476 | Yes | 30
13 | 0.56 | 161 | 90.16 | 16.1 | 8.1 | 36.1825 | Yes | 30
14 | 0.58 | 161 | 93.38 | 15.8 | 7.7 | 31.9109 | Yes | 30
15 | 0.52 | 161 | 83.72 | 15.8 | 7.4 | 28.3568 | Yes | 30
16 | 0.57 | 161 | 91.77 | 16 | 7.3 | 27.1135 | Yes | 30
17 | 0.59 | 161 | 94.99 | 16.4 | 7.3 | 26.4572 | Yes | 30
18 | 0.62 | 161 | 99.82 | 16.5 | 7.5 | 28.4064 | Yes | 30
19 | 0.67 | 161 | 107.87 | 16.9 | 7.3 | 25.8206 | Yes | 30
20 | 0.81 | 161 | 130.41 | 15.8 | 7.4 | 29.3111 | Yes | 30
21 | 0.7 | 161 | 112.7 | 16.5 | 7.9 | 33.2472 | Yes | 30
22 | 0.62 | 161 | 99.82 | 16.6 | 7.8 | 31.5379 | Yes | 30
23 | 0.63 | 161 | 101.43 | 16.6 | 7.8 | 31.5739 | Yes | 30
24 | 0.68 | 161 | 109.48 | 16.4 | 7.4 | 27.7437 | Yes | 30
25 | 0.66 | 161 | 106.26 | 16.2 | 7.9 | 33.764 | Yes | 30
26 | 0.76 | 161 | 122.36 | 16.1 | 7.9 | 34.378 | Yes | 30
27 | 0.73 | 161 | 117.53 | 16 | 7.8 | 33.238 | Yes | 30
28 | 0.5 | 161 | 80.5 | 17 | 7.5 | 27.0976 | Yes | 30
29 | 0.53 | 161 | 85.33 | 16.9 | 7.4 | 26.3739 | Yes | 30
30 | 0.6 | 161 | 96.6 | 17.1 | 7.5 | 27.2263 | Yes | 30
31 | 0.6 | 161 | 96.6 | 16.5 | 7.3 | 26.3106 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: