## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-07-23
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.112
2 |  |  | 0.11
3 |  |  | 0.138
4 |  |  | 0.224
5 |  |  | 0.258
6 |  |  | 0.185
7 |  |  | 0.167
8 |  |  | 0.164
9 |  |  | 0.15
10 |  |  | 0.13
11 |  |  | 0.12
12 |  |  | 0.11
13 |  |  | 0.11
14 |  |  | 0.11
15 |  |  | 0.11
16 |  |  | 0.11
17 |  |  | 0.11
18 |  |  | 0.1
19 |  |  | 0.11
20 |  |  | 0.11
21 |  |  | 0.11
22 |  |  | 0.11
23 |  |  | 0.11
24 |  |  | 0.113
25 |  |  | 0.116
26 |  |  | 0.114
27 |  |  | 0.11
28 |  |  | 0.12
29 |  |  | 0.126
30 |  |  | 0.15
31 |  |  | 0.122
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.81 | 161 | 130.41 | 17.9 | 7.7 | 28.4734 | Yes | 30
2 | 1.02 | 161 | 164.22 | 17.7 | 7.7 | 29.5564 | Yes | 30
3 | 0.98 | 161 | 157.78 | 17.8 | 7.9 | 31.4752 | Yes | 30
4 | 0.91 | 161 | 146.51 | 17.9 | 7.6 | 27.7502 | Yes | 30
5 | 0.93 | 161 | 149.73 | 18.1 | 7.5 | 26.4419 | Yes | 30
6 | 0.86 | 161 | 138.46 | 18.1 | 7.5 | 26.231 | Yes | 30
7 | 0.73 | 161 | 117.53 | 18.2 | 7.6 | 26.6444 | Yes | 30
8 | 0.71 | 161 | 114.31 | 18 | 7.7 | 27.9624 | Yes | 30
9 | 0.76 | 161 | 122.36 | 18.3 | 8 | 30.8099 | Yes | 30
10 | 0.61 | 161 | 98.21 | 18.4 | 8.1 | 31.2221 | Yes | 30
11 | 0.68 | 161 | 109.48 | 18.1 | 8 | 30.9404 | Yes | 30
12 | 0.65 | 161 | 104.65 | 18.2 | 7.9 | 29.5149 | Yes | 30
13 | 0.67 | 161 | 107.87 | 18.4 | 7.8 | 28.1257 | Yes | 30
14 | 0.67 | 161 | 107.87 | 18.6 | 7.7 | 26.739 | Yes | 30
15 | 0.79 | 161 | 127.19 | 18.8 | 7.7 | 26.7478 | Yes | 30
16 | 0.6 | 161 | 96.6 | 18.9 | 7.9 | 28.0053 | Yes | 30
17 | 0.56 | 161 | 90.16 | 19.1 | 8.2 | 30.7467 | Yes | 30
18 | 0.6 | 161 | 96.6 | 18.8 | 8 | 29.2596 | Yes | 30
19 | 0.7 | 161 | 112.7 | 18.5 | 8.3 | 33.7412 | Yes | 30
20 | 0.95 | 161 | 152.95 | 18.9 | 7.8 | 28.0847 | Yes | 30
21 | 1.01 | 161 | 162.61 | 19.4 | 8 | 29.4561 | Yes | 30
22 | 1.09 | 161 | 175.49 | 19.4 | 8 | 29.7261 | Yes | 30
23 | 0.93 | 161 | 149.73 | 19.6 | 7.9 | 27.7508 | Yes | 30
24 | 0.88 | 161 | 141.68 | 19.6 | 7.9 | 27.5927 | Yes | 30
25 | 0.9 | 161 | 144.9 | 19.5 | 7.9 | 27.8415 | Yes | 30
26 | 0.86 | 161 | 138.46 | 19.6 | 7.8 | 26.5246 | Yes | 30
27 | 0.93 | 161 | 149.73 | 19.6 | 7.7 | 25.761 | Yes | 30
28 | 0.81 | 161 | 130.41 | 19.8 | 7.9 | 27.0087 | Yes | 30
29 | 0.67 | 161 | 107.87 | 20.1 | 8 | 27.0382 | Yes | 30
30 | 0.95 | 161 | 152.95 | 19.6 | 7.8 | 26.7992 | Yes | 30
31 | 0.97 | 161 | 156.17 | 19.6 | 7.6 | 24.9327 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: