## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-08-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.11
2 |  |  | 0.12
3 |  |  | 0.12
4 |  |  | 0.12
5 |  |  | 0.13
6 |  |  | 0.12
7 |  |  | 0.12
8 |  |  | 0.12
9 |  |  | 0.13
10 |  |  | 0.12
11 |  |  | 0.12
12 |  |  | 0.12
13 |  |  | 0.12
14 |  |  | 0.13
15 |  |  | 0.15
16 |  |  | 0.15
17 |  |  | 0.15
18 |  |  | 0.13
19 |  |  | 0.13
20 |  |  | 0.12
21 |  |  | 0.12
22 |  |  | 0.17
23 |  |  | 0.12
24 |  |  | 0.1
25 |  |  | 0.72
26 |  |  | 0.65
27 |  |  | 0.56
28 |  |  | 0.5
29 |  |  | 0.35
30 |  |  | 0.56
31 |  |  | 0.39
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-08-23 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.83 | 161 | 133.63 | 19.6 | 7.5 | 23.6368 | Yes | 30
2 | 0.79 | 161 | 127.19 | 19.7 | 7.5 | 23.3707 | Yes | 30
3 | 0.83 | 161 | 133.63 | 19.7 | 7.7 | 25.2973 | Yes | 30
4 | 0.82 | 161 | 132.02 | 19.9 | 8.3 | 31.1584 | Yes | 30
5 | 0.9 | 161 | 144.9 | 19.9 | 8.2 | 30.2998 | Yes | 30
6 | 0.79 | 161 | 127.19 | 19.9 | 8.1 | 28.8323 | Yes | 30
7 | 0.75 | 161 | 120.75 | 19.8 | 7.8 | 25.844 | Yes | 30
8 | 0.68 | 161 | 109.48 | 20.4 | 7.7 | 23.7237 | Yes | 30
9 | 0.61 | 161 | 98.21 | 20.6 | 7.7 | 23.2193 | Yes | 30
10 | 0.76 | 161 | 122.36 | 20.3 | 7.6 | 23.2205 | Yes | 30
11 | 0.8 | 161 | 128.8 | 20.3 | 7.5 | 22.4714 | Yes | 30
12 | 0.7 | 161 | 112.7 | 20.7 | 7.4 | 20.8277 | Yes | 30
13 | 0.82 | 161 | 132.02 | 20.5 | 7.4 | 21.4049 | Yes | 30
14 | 0.68 | 161 | 109.48 | 20.7 | 7.4 | 20.7797 | Yes | 30
15 | 0.68 | 161 | 109.48 | 21.1 | 7.3 | 19.4793 | Yes | 30
16 | 0.57 | 161 | 91.77 | 21.2 | 7.4 | 19.8354 | Yes | 30
17 | 0.71 | 161 | 114.31 | 21.4 | 7.3 | 19.1538 | Yes | 30
18 | 0.68 | 161 | 109.48 | 21.5 | 7.3 | 18.9585 | Yes | 30
19 | 0.75 | 161 | 120.75 | 20.7 | 7.2 | 19.4321 | Yes | 30
20 | 0.67 | 161 | 107.87 | 21.1 | 7.2 | 18.738 | Yes | 30
21 | 0.69 | 161 | 111.09 | 21 | 7.2 | 18.9093 | Yes | 30
22 | 0.72 | 161 | 115.92 | 21 | 7.4 | 20.4569 | Yes | 30
23 | 0.77 | 161 | 123.97 | 21 | 7.5 | 21.3616 | Yes | 30
24 | 0.88 | 161 | 141.68 | 20.8 | 7.6 | 22.7639 | Yes | 30
25 | 0.76 | 161 | 122.36 | 21.2 | 7.7 | 22.6881 | Yes | 30
26 | 0.82 | 161 | 132.02 | 20.9 | 7.5 | 21.6305 | Yes | 30
27 | 0.84 | 161 | 135.24 | 20.8 | 7.4 | 21.0242 | Yes | 30
28 | 0.73 | 161 | 117.53 | 20.7 | 7.4 | 20.8999 | Yes | 30
29 | 0.78 | 161 | 125.58 | 20.3 | 7.3 | 20.8013 | Yes | 30
30 | 0.64 | 161 | 103.04 | 20 | 7.5 | 22.512 | Yes | 30
31 | 0.79 | 161 | 127.19 | 19.9 | 7.6 | 23.9359 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: