## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-09-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.27
2 |  |  | 0.19
3 |  |  | 0.35
4 |  |  | 0.24
5 |  |  | 0.19
6 |  |  | 0.16
7 |  |  | 0.21
8 |  |  | 0.17
9 |  |  | 0.15
10 |  |  | 0.82
11 |  |  | 0.64
12 |  |  | 0.57
13 |  |  | 0.59
14 |  |  | 0.34
15 |  |  | 0.22
16 |  |  | 0.2
17 |  |  | 0.54
18 |  |  | 0.34
19 |  |  | 0.21
20 |  |  | 0.47
21 |  |  | 0.33
22 |  |  | 0.23
23 |  |  | 0.24
24 |  |  | 0.18
25 |  |  | 0.15
26 |  |  | 0.17
27 |  |  | 0.23
28 |  |  | 0.17
29 |  |  | 0.14
30 |  |  | 0.13
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.96 | 161 | 154.56 | 19.6 | 7.6 | 24.9041 | Yes | 30
2 | 0.99 | 161 | 159.39 | 19.8 | 7.8 | 26.5638 | Yes | 30
3 | 0.99 | 161 | 159.39 | 20 | 7.7 | 25.2519 | Yes | 30
4 | 1.05 | 161 | 169.05 | 19.5 | 7.8 | 27.2895 | Yes | 30
5 | 1 | 161 | 161 | 19.4 | 7.9 | 28.3503 | Yes | 30
6 | 0.86 | 161 | 138.46 | 18.9 | 7.6 | 25.8043 | Yes | 30
7 | 0.89 | 161 | 143.29 | 18.7 | 7.6 | 26.2426 | Yes | 30
8 | 0.89 | 161 | 143.29 | 19.2 | 7.5 | 24.4486 | Yes | 30
9 | 0.89 | 161 | 143.29 | 18.9 | 7.8 | 27.8928 | Yes | 30
10 | 0.86 | 161 | 138.46 | 19.1 | 7.7 | 26.4264 | Yes | 30
11 | 0.94 | 161 | 151.34 | 18.9 | 7.4 | 24.171 | Yes | 30
12 | 0.86 | 161 | 138.46 | 18.6 | 7.2 | 22.6787 | Yes | 30
13 | 0.97 | 161 | 156.17 | 18.5 | 7.4 | 24.9147 | Yes | 30
14 | 1.05 | 161 | 169.05 | 18.4 | 7.7 | 28.3022 | Yes | 30
15 | 0.82 | 161 | 132.02 | 18.6 | 8.1 | 31.5541 | Yes | 30
16 | 0.87 | 161 | 140.07 | 18.4 | 8.2 | 33.3724 | Yes | 30
17 | 0.71 | 161 | 114.31 | 18.3 | 7.8 | 28.4441 | Yes | 30
18 | 0.56 | 161 | 90.16 | 18.1 | 7.6 | 26.3068 | Yes | 30
19 | 0.5 | 161 | 80.5 | 17.5 | 7.5 | 26.205 | Yes | 30
20 | 0.44 | 161 | 70.84 | 17.6 | 7.4 | 24.9062 | Yes | 30
21 | 0.46 | 161 | 74.06 | 17.2 | 7.7 | 28.6688 | Yes | 30
22 | 0.54 | 161 | 86.94 | 17.2 | 7.7 | 28.9318 | Yes | 30
23 | 0.47 | 161 | 75.67 | 17.6 | 7.8 | 29.0012 | Yes | 30
24 | 0.52 | 161 | 83.72 | 17.5 | 7.8 | 29.3627 | Yes | 30
25 | 0.62 | 161 | 99.82 | 17.5 | 7.9 | 30.8213 | Yes | 30
26 | 0.83 | 161 | 133.63 | 17.1 | 7.6 | 29.0089 | Yes | 30
27 | 0.78 | 161 | 125.58 | 17.8 | 7.7 | 28.5664 | Yes | 30
28 | 0.71 | 161 | 114.31 | 17.4 | 7.8 | 30.2069 | Yes | 30
29 | 0.49 | 161 | 78.89 | 17.4 | 7.7 | 28.3851 | Yes | 30
30 | 0.5 | 161 | 80.5 | 16.9 | 7.7 | 29.3832 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: