## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-10-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.12
2 |  |  | 0.12
3 |  |  | 0.11
4 |  |  | 0.11
5 |  |  | 0.11
6 |  |  | 0.11
7 |  |  | 0.11
8 |  |  | 0.1
9 |  |  | 0.1
10 |  |  | 0.1
11 |  |  | 0.1
12 |  |  | 0.1
13 |  |  | 0.1
14 |  |  | 0.1
15 |  |  | 0.12
16 |  |  | 0.17
17 |  |  | 0.09
18 |  |  | 0.09
19 |  |  | 0.09
20 |  |  | 0.07
21 |  |  | 0.21
22 |  |  | 0.18
23 |  |  | 0.14
24 |  |  | 0.13
25 |  |  | 0.15
26 |  |  | 0.19
27 |  |  | 0.2
28 |  |  | 0.15
29 |  |  | 0.11
30 |  |  | 0.1
31 |  |  | 0.09
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2023-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.37 | 161 | 59.57 | 17 | 7.7 | 28.7577 | Yes | 30
2 | 0.36 | 161 | 57.96 | 17.2 | 7.6 | 27.3094 | Yes | 30
3 | 0.4 | 161 | 64.4 | 17.4 | 8 | 31.4017 | Yes | 30
4 | 0.96 | 161 | 154.56 | 17.2 | 7.8 | 31.4972 | Yes | 30
5 | 0.97 | 161 | 156.17 | 17.2 | 7.7 | 30.3861 | Yes | 30
6 | 1.07 | 161 | 172.27 | 17.1 | 7.6 | 29.8142 | Yes | 30
7 | 1.1 | 161 | 177.1 | 17.5 | 7.6 | 29.1276 | Yes | 30
8 | 0.88 | 161 | 141.68 | 17.9 | 7.7 | 28.7019 | Yes | 30
9 | 0.87 | 161 | 140.07 | 17.6 | 7.6 | 28.1837 | Yes | 30
10 | 0.9 | 161 | 144.9 | 17.1 | 7.5 | 28.1759 | Yes | 30
11 | 0.71 | 161 | 114.31 | 17.4 | 7.8 | 30.2069 | Yes | 30
12 | 0.68 | 161 | 109.48 | 17.2 | 7.8 | 30.5083 | Yes | 30
13 | 0.64 | 161 | 103.04 | 16.3 | 7.7 | 31.076 | Yes | 30
14 | 0.45 | 161 | 72.45 | 17.5 | 7.6 | 27.0432 | Yes | 30
15 | 0.24 | 161 | 38.64 | 17.5 | 8 | 30.6295 | Yes | 30
16 | 0.23 | 161 | 37.03 | 17.7 | 8 | 30.1889 | Yes | 30
17 | 0.67 | 161 | 107.87 | 16.8 | 7.9 | 32.4783 | Yes | 30
18 | 0.77 | 161 | 123.97 | 16.6 | 7.8 | 32.0811 | Yes | 30
19 | 0.62 | 161 | 99.82 | 17.3 | 7.7 | 29.0027 | Yes | 30
20 | 0.91 | 161 | 146.51 | 17 | 7.8 | 31.7388 | Yes | 30
21 | 0.92 | 161 | 148.12 | 17 | 7.7 | 30.6194 | Yes | 30
22 | 1 | 161 | 161 | 16.7 | 7.4 | 28.2049 | Yes | 30
23 | 0.86 | 161 | 138.46 | 17.1 | 7.5 | 28.0474 | Yes | 30
24 | 1 | 161 | 161 | 16.8 | 7.6 | 30.1756 | Yes | 30
25 | 1.02 | 161 | 164.22 | 16.8 | 7.5 | 29.1432 | Yes | 30
26 | 1.01 | 161 | 162.61 | 16.3 | 7.7 | 32.4131 | Yes | 30
27 | 0.73 | 161 | 117.53 | 16.4 | 7.6 | 30.0528 | Yes | 30
28 | 0.62 | 161 | 99.82 | 15.6 | 7.6 | 31.3058 | Yes | 30
29 | 0.54 | 161 | 86.94 | 15.8 | 7.8 | 32.9636 | Yes | 30
30 | 0.35 | 161 | 56.35 | 15.3 | 7.8 | 33.3512 | Yes | 30
31 | 0.49 | 161 | 78.89 | 15.2 | 7.4 | 29.4161 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: