## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2//24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.101
2 |  |  | 0.13
3 |  |  | 0.11
4 |  |  | 0.13
5 |  |  | 0.17
6 |  |  | 0.15
7 |  |  | 0.18
8 |  |  | 0.18
9 |  |  | 0.13
10 |  |  | 0.14
11 |  |  | 0.15
12 |  |  | 0.13
13 |  |  | 0.17
14 |  |  | 0.14
15 |  |  | 0.19
16 |  |  | 0.18
17 |  |  | 0.13
18 |  |  | 0.18
19 |  |  | 0.14
20 |  |  | 0.16
21 |  |  | 0.18
22 |  |  | 0.13
23 |  |  | 0.15
24 |  |  | 0.15
25 |  |  | 0.14
26 |  |  | 0.15
27 |  |  | 0.14
28 |  |  | 0.14
29 |  |  | 0.21
30 |  |  | 0
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-02-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.72 | 161 | 115.92 | 13.8 | 7.5 | 34.4013 | Yes | 30
2 | 0.76 | 161 | 122.36 | 13.8 | 7.5 | 34.558 | Yes | 30
3 | 0.78 | 161 | 125.58 | 13.2 | 7.4 | 34.7396 | Yes | 30
4 | 0.71 | 161 | 114.31 | 13.7 | 7.4 | 33.3362 | Yes | 30
5 | 0.78 | 161 | 125.58 | 13.5 | 7.3 | 32.8166 | Yes | 30
6 | 0.86 | 161 | 138.46 | 13 | 7.3 | 34.2375 | Yes | 30
7 | 0.66 | 161 | 106.26 | 12.9 | 7.3 | 33.6915 | Yes | 30
8 | 0.91 | 161 | 146.51 | 12.9 | 7.4 | 35.9667 | Yes | 30
9 | 0.85 | 161 | 136.85 | 13.2 | 7.6 | 37.6997 | Yes | 30
10 | 0.74 | 161 | 119.14 | 14.2 | 7.5 | 33.5737 | Yes | 30
11 | 0.8 | 161 | 128.8 | 13.4 | 7.7 | 38.3817 | Yes | 30
12 | 0.85 | 161 | 136.85 | 13.4 | 7.6 | 37.2023 | Yes | 30
13 | 0.89 | 161 | 143.29 | 13.2 | 7.5 | 36.4994 | Yes | 30
14 | 0.89 | 161 | 143.29 | 13.7 | 7.5 | 35.3062 | Yes | 30
15 | 0.86 | 161 | 138.46 | 13.3 | 7.4 | 34.8243 | Yes | 30
16 | 0.97 | 161 | 156.17 | 12.9 | 7.5 | 37.5736 | Yes | 30
17 | 0.87 | 161 | 140.07 | 13.9 | 7.5 | 34.7605 | Yes | 30
18 | 0.96 | 161 | 154.56 | 13.4 | 7.7 | 39.084 | Yes | 30
19 | 0.82 | 161 | 132.02 | 14.2 | 7.6 | 35.1558 | Yes | 30
20 | 0.89 | 161 | 143.29 | 13.1 | 7.6 | 38.1234 | Yes | 30
21 | 0.87 | 161 | 140.07 | 13.8 | 7.5 | 34.9925 | Yes | 30
22 | 0.9 | 161 | 144.9 | 13.6 | 7.5 | 35.5821 | Yes | 30
23 | 0.9 | 161 | 144.9 | 13.1 | 7.4 | 35.4513 | Yes | 30
24 | 0.92 | 161 | 148.12 | 13.4 | 7.3 | 33.5661 | Yes | 30
25 | 0.79 | 161 | 127.19 | 14.4 | 7.4 | 32.1081 | Yes | 30
26 | 0.76 | 161 | 122.36 | 13.3 | 7.2 | 31.9757 | Yes | 30
27 | 0.82 | 161 | 132.02 | 13 | 7.6 | 38.074 | Yes | 30
28 | 0.9 | 161 | 144.9 | 13.3 | 7.8 | 40.5441 | Yes | 30
29 | 0.95 | 161 | 152.95 | 12.6 | 7.7 | 41.1671 | Yes | 30
30 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: