## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-03-24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.79
2 |  |  | 0.62
3 |  |  | 0.43
4 |  |  | 0.31
5 |  |  | 0.19
6 |  |  | 0.16
7 |  |  | 0.13
8 |  |  | 0.11
9 |  |  | 0.17
10 |  |  | 0.12
11 |  |  | 0.12
12 |  |  | 0.12
13 |  |  | 0.15
14 |  |  | 0.3
15 |  |  | 0.22
16 |  |  | 0.14
17 |  |  | 0.12
18 |  |  | 0.11
19 |  |  | 0.11
20 |  |  | 0.11
21 |  |  | 0.11
22 |  |  | 0.13
23 |  |  | 0.12
24 |  |  | 0.14
25 |  |  | 0.16
26 |  |  | 0.13
27 |  |  | 0.13
28 |  |  | 0.12
29 |  |  | 0.13
30 |  |  | 0.13
31 |  |  | 0.16
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-03-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.13 | 161 | 181.93 | 11.7 | 7.5 | 41.7015 | Yes | 30
2 | 1.11 | 161 | 178.71 | 1.8 | 7.5 | 81.2194 | Yes | 30
3 | 0.89 | 161 | 143.29 | 12.7 | 7.5 | 37.7321 | Yes | 30
4 | 0.73 | 161 | 117.53 | 12.6 | 7.5 | 37.3005 | Yes | 30
5 | 0.67 | 161 | 107.87 | 12.3 | 7.4 | 36.8007 | Yes | 30
6 | 0.77 | 161 | 123.97 | 11.7 | 7.3 | 37.3722 | Yes | 30
7 | 0.7 | 161 | 112.7 | 11.7 | 7.3 | 37.0836 | Yes | 30
8 | 0.82 | 161 | 132.02 | 12.3 | 7.3 | 36.1511 | Yes | 30
9 | 0.67 | 161 | 107.87 | 12.4 | 7.2 | 34.1442 | Yes | 30
10 | 0.68 | 161 | 109.48 | 13 | 7.4 | 34.8072 | Yes | 30
11 | 0.73 | 161 | 117.53 | 11.7 | 7.2 | 35.9491 | Yes | 30
12 | 0.7 | 161 | 112.7 | 12.7 | 7.4 | 35.5894 | Yes | 30
13 | 0.67 | 161 | 107.87 | 12.4 | 7.3 | 35.3305 | Yes | 30
14 | 0.7 | 161 | 112.7 | 12.1 | 7.2 | 34.9212 | Yes | 30
15 | 0.65 | 161 | 104.65 | 12.4 | 7.7 | 40.4745 | Yes | 30
16 | 0.67 | 161 | 107.87 | 12.9 | 7.2 | 32.5049 | Yes | 30
17 | 0.55 | 161 | 88.55 | 13.1 | 7.2 | 31.6394 | Yes | 30
18 | 0.53 | 161 | 85.33 | 13.6 | 7.32 | 31.9197 | Yes | 30
19 | 0.55 | 161 | 88.55 | 13.5 | 7.2 | 30.8064 | Yes | 30
20 | 0.57 | 161 | 91.77 | 13.8 | 7.8 | 37.7815 | Yes | 30
21 | 0.45 | 161 | 72.45 | 14.1 | 7.4 | 31.513 | Yes | 30
22 | 0.5 | 161 | 80.5 | 14 | 7.2 | 29.6258 | Yes | 30
23 | 0.45 | 161 | 72.45 | 14.8 | 7.4 | 30.075 | Yes | 30
24 | 0.47 | 161 | 75.67 | 14 | 7.4 | 31.7962 | Yes | 30
25 | 0.45 | 161 | 72.45 | 13.9 | 7.4 | 31.9361 | Yes | 30
26 | 0.41 | 161 | 66.01 | 14.1 | 7.4 | 31.3698 | Yes | 30
27 | 0.45 | 161 | 72.45 | 14.6 | 7.9 | 36.67 | Yes | 30
28 | 0.51 | 161 | 82.11 | 14.7 | 7.4 | 30.4842 | Yes | 30
29 | 0.55 | 161 | 88.55 | 14.6 | 7.3 | 29.7065 | Yes | 30
30 | 0.62 | 161 | 99.82 | 14.1 | 7.4 | 32.1289 | Yes | 30
31 | 0.79 | 161 | 127.19 | 14.1 | 7.3 | 31.5661 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: