## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-08-24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.75
2 |  |  | 0.58
3 |  |  | 0.58
4 |  |  | 0.61
5 |  |  | 0.5
6 |  |  | 0.69
7 |  |  | 0.69
8 |  |  | 0.79
9 |  |  | 0.54
10 |  |  | 0.5
11 |  |  | 0.46
12 |  |  | 0.48
13 |  |  | 0.36
14 |  |  | 0.4
15 |  |  | 0.36
16 |  |  | 0.34
17 |  |  | 0.32
18 |  |  | 0.24
19 |  |  | 0.31
20 |  |  | 0.3
21 |  |  | 0.31
22 |  |  | 0.31
23 |  |  | 0.41
24 |  |  | 0.53
25 |  |  | 0.5
26 |  |  | 0.37
27 |  |  | 0.51
28 |  |  | 0.44
29 |  |  | 0.36
30 |  |  | 0.42
31 |  |  | 0.33
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-08-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.64 | 161 | 103.04 | 19.6 | 7.5 | 23.1265 | Yes | 30
2 | 0.59 | 161 | 94.99 | 20.1 | 7.5 | 22.2326 | Yes | 30
3 | 0.59 | 161 | 94.99 | 20 | 7.4 | 21.5603 | Yes | 30
4 | 0.68 | 161 | 109.48 | 19.9 | 7.4 | 21.9324 | Yes | 30
5 | 0.62 | 161 | 99.82 | 19.9 | 7.3 | 20.9801 | Yes | 30
6 | 0.72 | 161 | 115.92 | 19.8 | 7.4 | 22.1826 | Yes | 30
7 | 0.64 | 161 | 103.04 | 19.7 | 7.4 | 22.1279 | Yes | 30
8 | 0.71 | 161 | 114.31 | 20 | 7.4 | 21.8604 | Yes | 30
9 | 0.64 | 161 | 103.04 | 20.1 | 7.4 | 21.5391 | Yes | 30
10 | 0.65 | 161 | 104.65 | 19.9 | 7.4 | 21.8567 | Yes | 30
11 | 0.53 | 161 | 85.33 | 20.4 | 7.4 | 20.8413 | Yes | 30
12 | 0.57 | 161 | 91.77 | 20.1 | 7.4 | 21.366 | Yes | 30
13 | 0.59 | 161 | 94.99 | 19.8 | 7.4 | 21.8531 | Yes | 30
14 | 0.6 | 161 | 96.6 | 19.9 | 7.4 | 21.7312 | Yes | 30
15 | 0.59 | 161 | 94.99 | 19.9 | 7.3 | 20.9077 | Yes | 30
16 | 0.56 | 161 | 90.16 | 19.9 | 7.4 | 21.6314 | Yes | 30
17 | 0.62 | 161 | 99.82 | 19.8 | 8 | 27.4295 | Yes | 30
18 | 0.65 | 161 | 104.65 | 19.8 | 8.1 | 28.5655 | Yes | 30
19 | 0.67 | 161 | 107.87 | 19.5 | 8 | 28.146 | Yes | 30
20 | 0.66 | 161 | 106.26 | 19.8 | 7.8 | 25.579 | Yes | 30
21 | 0.67 | 161 | 107.87 | 19.7 | 7.5 | 23.0507 | Yes | 30
22 | 0.85 | 161 | 136.85 | 19.5 | 7.8 | 26.6724 | Yes | 30
23 | 0.73 | 161 | 117.53 | 19.2 | 7.4 | 23.1238 | Yes | 30
24 | 0.79 | 161 | 127.19 | 19 | 7.2 | 21.8985 | Yes | 30
25 | 0.79 | 161 | 127.19 | 18.4 | 7.3 | 23.6701 | Yes | 30
26 | 0.73 | 161 | 117.53 | 18.8 | 7.5 | 24.6576 | Yes | 30
27 | 0.89 | 161 | 143.29 | 19.1 | 8.1 | 30.7634 | Yes | 30
28 | 0.75 | 161 | 120.75 | 18.9 | 7.3 | 22.782 | Yes | 30
29 | 0.81 | 161 | 130.41 | 18.5 | 7.7 | 27.3531 | Yes | 30
30 | 0.8 | 161 | 128.8 | 19 | 7.5 | 24.5248 | Yes | 30
31 | 0.76 | 161 | 122.36 | 19.3 | 7.4 | 23.0481 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: