## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-09-24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.32
2 |  |  | 0.35
3 |  |  | 0.34
4 |  |  | 0.34
5 |  |  | 0.35
6 |  |  | 0.66
7 |  |  | 0.68
8 |  |  | 0.45
9 |  |  | 0.38
10 |  |  | 0.54
11 |  |  | 0.59
12 |  |  | 0.65
13 |  |  | 0.46
14 |  |  | 0.34
15 |  |  | 0.31
16 |  |  | 0.42
17 |  |  | 0.4
18 |  |  | 0.41
19 |  |  | 0.41
20 |  |  | 0.36
21 |  |  | 0.42
22 |  |  | 0.49
23 |  |  | 0.585
24 |  |  | 0.45
25 |  |  | 0.46
26 |  |  | 0.48
27 |  |  | 0.51
28 |  |  | 0.52
29 |  |  | 0.49
30 |  |  | 0.52
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-09-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.68 | 161 | 109.48 | 19.5 | 7.6 | 24.2796 | Yes | 30
2 | 0.63 | 161 | 101.43 | 19.4 | 7.9 | 27.1767 | Yes | 30
3 | 0.75 | 161 | 120.75 | 19.3 | 7.6 | 24.8063 | Yes | 30
4 | 0.83 | 161 | 133.63 | 19.2 | 7.2 | 21.7049 | Yes | 30
5 | 0.79 | 161 | 127.19 | 19.2 | 7.5 | 24.1697 | Yes | 30
6 | 0.8 | 161 | 128.8 | 19.4 | 7.3 | 22.1546 | Yes | 30
7 | 0.62 | 161 | 99.82 | 20.1 | 7.3 | 20.6986 | Yes | 30
8 | 0.59 | 161 | 94.99 | 20 | 7.7 | 24.1198 | Yes | 30
9 | 0.67 | 161 | 107.87 | 19.9 | 7.9 | 26.4022 | Yes | 30
10 | 0.75 | 161 | 120.75 | 19.7 | 7.6 | 24.1487 | Yes | 30
11 | 0.6 | 161 | 96.6 | 19.8 | 7.6 | 23.5774 | Yes | 30
12 | 0.69 | 161 | 111.09 | 19.5 | 7.3 | 21.7288 | Yes | 30
13 | 0.74 | 161 | 119.14 | 19 | 7.7 | 26.2412 | Yes | 30
14 | 0.8 | 161 | 128.8 | 19 | 8 | 29.5376 | Yes | 30
15 | 0.69 | 161 | 111.09 | 18.9 | 7.7 | 26.267 | Yes | 30
16 | 0.84 | 161 | 135.24 | 18.5 | 7.4 | 24.5461 | Yes | 30
17 | 0.98 | 161 | 157.78 | 18.8 | 7.4 | 24.4458 | Yes | 30
18 | 0.92 | 161 | 148.12 | 18.8 | 7.4 | 24.2781 | Yes | 30
19 | 1.08 | 161 | 173.88 | 18.6 | 7.4 | 25.062 | Yes | 30
20 | 1.01 | 161 | 162.61 | 18.8 | 7.6 | 26.4278 | Yes | 30
21 | 1.06 | 161 | 170.66 | 18.3 | 8 | 31.8808 | Yes | 30
22 | 0.98 | 161 | 157.78 | 18.4 | 8.2 | 33.7924 | Yes | 30
23 | 0.98 | 161 | 157.78 | 18.6 | 7.3 | 23.8689 | Yes | 30
24 | 0.92 | 161 | 148.12 | 18.6 | 7.8 | 28.5558 | Yes | 30
25 | 0.76 | 161 | 122.36 | 19.1 | 7.5 | 24.249 | Yes | 30
26 | 0.62 | 161 | 99.82 | 18.4 | 7.7 | 26.9451 | Yes | 30
27 | 0.46 | 161 | 74.06 | 18.3 | 7.4 | 23.8167 | Yes | 30
28 | 0.39 | 161 | 62.79 | 18.3 | 7.5 | 24.5245 | Yes | 30
29 | 0.28 | 161 | 45.08 | 18.1 | 7.7 | 26.4433 | Yes | 30
30 | 0.36 | 161 | 57.96 | 17.7 | 7.7 | 27.4109 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: