## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-10-24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.6
2 |  |  | 0.62
3 |  |  | 0.61
4 |  |  | 0.62
5 |  |  | 0.62
6 |  |  | 0.62
7 |  |  | 0.62
8 |  |  | 0.61
9 |  |  | 0.61
10 |  |  | 0.62
11 |  |  | 0.61
12 |  |  | 0.62
13 |  |  | 0.62
14 |  |  | 0.64
15 |  |  | 0.63
16 |  |  | 0.63
17 |  |  | 0.62
18 |  |  | 0.63
19 |  |  | 0.61
20 |  |  | 0.61
21 |  |  | 0.61
22 |  |  | 0.6
23 |  |  | 0.64
24 |  |  | 0.6
25 |  |  | 0.61
26 |  |  | 0.62
27 |  |  | 0.62
28 |  |  | 0.61
29 |  |  | 0.64
30 |  |  | 0.55
31 |  |  | 0.67
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-10-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.39 | 161 | 62.79 | 17.7 | 7.5 | 25.5323 | Yes | 30
2 | 0.5 | 161 | 80.5 | 17.7 | 7.4 | 24.9103 | Yes | 30
3 | 0.72 | 161 | 115.92 | 17.4 | 7.3 | 25.1123 | Yes | 30
4 | 0.68 | 161 | 109.48 | 17.4 | 7.5 | 26.9301 | Yes | 30
5 | 0.77 | 161 | 123.97 | 17.7 | 8 | 32.1042 | Yes | 30
6 | 0.62 | 161 | 99.82 | 18.2 | 7.8 | 28.3422 | Yes | 30
7 | 0.77 | 161 | 123.97 | 17.7 | 7.8 | 29.8111 | Yes | 30
8 | 0.79 | 161 | 127.19 | 17.9 | 7.4 | 25.4088 | Yes | 30
9 | 0.77 | 161 | 123.97 | 18 | 7.5 | 26.1367 | Yes | 30
10 | 0.77 | 161 | 123.97 | 17.7 | 7.6 | 27.6778 | Yes | 30
11 | 0.75 | 161 | 120.75 | 17.8 | 7.5 | 26.4289 | Yes | 30
12 | 0.71 | 161 | 114.31 | 17.9 | 7.6 | 27.123 | Yes | 30
13 | 0.57 | 161 | 91.77 | 18.2 | 7.5 | 25.2045 | Yes | 30
14 | 0.62 | 161 | 99.82 | 17.6 | 7.6 | 27.39 | Yes | 30
15 | 0.6 | 161 | 96.6 | 17.5 | 7.4 | 25.5378 | Yes | 30
16 | 0.63 | 161 | 101.43 | 17.6 | 7.2 | 23.6245 | Yes | 30
17 | 0.64 | 161 | 103.04 | 17.2 | 7.4 | 26.1764 | Yes | 30
18 | 0.68 | 161 | 109.48 | 17.6 | 7.3 | 24.664 | Yes | 30
19 | 0.65 | 161 | 104.65 | 18 | 7.2 | 23.0502 | Yes | 30
20 | 0.68 | 161 | 109.48 | 17.5 | 7.9 | 31.0327 | Yes | 30
21 | 0.69 | 161 | 111.09 | 17.5 | 7.8 | 29.9376 | Yes | 30
22 | 0.87 | 161 | 140.07 | 17.1 | 7.6 | 29.1417 | Yes | 30
23 | 0.88 | 161 | 141.68 | 17.1 | 7.5 | 28.1116 | Yes | 30
24 | 0.8 | 161 | 128.8 | 17.4 | 7.3 | 25.3435 | Yes | 30
25 | 0.83 | 161 | 133.63 | 17.1 | 7.6 | 29.0089 | Yes | 30
26 | 0.77 | 161 | 123.97 | 17.6 | 7.5 | 26.8467 | Yes | 30
27 | 0.69 | 161 | 111.09 | 17.5 | 7.9 | 31.068 | Yes | 30
28 | 0.78 | 161 | 125.58 | 17.2 | 8 | 33.2294 | Yes | 30
29 | 0.81 | 161 | 130.41 | 17.1 | 7.3 | 25.8883 | Yes | 30
30 | 0.82 | 161 | 132.02 | 16.8 | 7.5 | 28.4854 | Yes | 30
31 | 0.84 | 161 | 135.24 | 16.7 | 7.3 | 26.6831 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: