## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-11-24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.7
2 |  |  | 0.69
3 |  |  | 0.61
4 |  |  | 0.52
5 |  |  | 0.63
6 |  |  | 0.77
7 |  |  | 0.76
8 |  |  | 0.57
9 |  |  | 0.3
10 |  |  | 0.32
11 |  |  | 0.43
12 |  |  | 0.3
13 |  |  | 0.31
14 |  |  | 0.25
15 |  |  | 0.55
16 |  |  | 0.65
17 |  |  | 0.36
18 |  |  | 0.25
19 |  |  | 0.3
20 |  |  | 0.28
21 |  |  | 0.26
22 |  |  | 0.37
23 |  |  | 0.31
24 |  |  | 0.24
25 |  |  | 0.21
26 |  |  | 0.21
27 |  |  | 0.19
28 |  |  | 0.27
29 |  |  | 0.19
30 |  |  | 0.14
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2024-11-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 161 | 132.02 | 17 | 7.5 | 28.1069 | Yes | 30
2 | 0.71 | 161 | 114.31 | 17.9 | 7.6 | 27.123 | Yes | 30
3 | 0.57 | 161 | 91.77 | 17.8 | 8 | 31.1728 | Yes | 30
4 | 0.75 | 161 | 120.75 | 17 | 7.5 | 27.8831 | Yes | 30
5 | 0.84 | 161 | 135.24 | 16.7 | 8 | 34.5891 | Yes | 30
6 | 0.8 | 161 | 128.8 | 17.2 | 7.4 | 26.66 | Yes | 30
7 | 0.8 | 161 | 128.8 | 16.7 | 7.6 | 29.6928 | Yes | 30
8 | 0.91 | 161 | 146.51 | 16.2 | 7.6 | 31.0878 | Yes | 30
9 | 0.76 | 161 | 122.36 | 16.6 | 7.6 | 29.7557 | Yes | 30
10 | 0.72 | 161 | 115.92 | 17 | 7.7 | 29.9292 | Yes | 30
11 | 0.7 | 161 | 112.7 | 17 | 7.5 | 27.7242 | Yes | 30
12 | 0.74 | 161 | 119.14 | 16.8 | 7.3 | 26.2034 | Yes | 30
13 | 0.77 | 161 | 123.97 | 16.5 | 7.3 | 26.8273 | Yes | 30
14 | 0.73 | 161 | 117.53 | 16.8 | 7.4 | 27.1655 | Yes | 30
15 | 0.62 | 161 | 99.82 | 17.8 | 7.2 | 23.2821 | Yes | 30
16 | 0.66 | 161 | 106.26 | 17 | 7.3 | 25.6186 | Yes | 30
17 | 0.56 | 161 | 90.16 | 18.1 | 8.2 | 32.8664 | Yes | 30
18 | 0.64 | 161 | 103.04 | 16.4 | 8 | 34.4937 | Yes | 30
19 | 0.68 | 161 | 109.48 | 16.2 | 7.3 | 27.0915 | Yes | 30
20 | 0.69 | 161 | 111.09 | 15.7 | 7.2 | 27.0221 | Yes | 30
21 | 0.57 | 161 | 91.77 | 16.3 | 7.3 | 26.5742 | Yes | 30
22 | 0.55 | 161 | 88.55 | 17.4 | 7.4 | 25.5629 | Yes | 30
23 | 0.51 | 161 | 82.11 | 17.4 | 7.2 | 23.6167 | Yes | 30
24 | 0.44 | 161 | 70.84 | 17.3 | 7.7 | 28.4128 | Yes | 30
25 | 0.56 | 161 | 90.16 | 16.2 | 7.6 | 29.8721 | Yes | 30
26 | 0.57 | 161 | 91.77 | 15.8 | 7.5 | 29.5975 | Yes | 30
27 | 0.52 | 161 | 83.72 | 16.4 | 8 | 34.0264 | Yes | 30
28 | 0.68 | 161 | 109.48 | 15.2 | 8.2 | 40.3988 | Yes | 30
29 | 0.65 | 161 | 104.65 | 15.4 | 7.7 | 33.0349 | Yes | 30
30 | 0.55 | 161 | 88.55 | 16.2 | 7.7 | 30.9649 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: