## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 12_24
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.12 | .
2 |  |  | 0.18
3 |  |  | 0.18
4 |  |  | 0.22
5 |  |  | 0.11
6 |  |  | 0.08
7 |  |  | 0.07
8 |  |  | 0.07
9 |  |  | 0.07
10 |  |  | 0.07
11 |  |  | 0.07
12 |  |  | 0.06
13 |  |  | 0.07
14 |  |  | 0.06
15 |  |  | 0.06
16 |  |  | 0.06
17 |  |  | 0.06
18 |  |  | 0.06
19 |  |  | 0.32
20 |  |  | 0.46
21 |  |  | 0.26
22 |  |  | 0.2
23 |  |  | 0.2
24 |  |  | 0.22
25 |  |  | 0.1
26 |  |  | 0.12
27 |  |  | 0.18
28 |  |  | 0.13
29 |  |  | 0.18
30 |  |  | 0.15
31 |  |  | 0.274
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 12_24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 161 | 99.82 | 15.5 | 7.5 | 30.3689 | Yes | 30
2 | 0.66 | 161 | 106.26 | 15.2 | 7.2 | 27.8461 | Yes | 30
3 | 0.76 | 161 | 122.36 | 14.4 | 7.3 | 30.8352 | Yes | 30
4 | 0.73 | 161 | 117.53 | 13.9 | 7.3 | 31.7721 | Yes | 30
5 | 0.89 | 161 | 143.29 | 13.6 | 7.2 | 31.8099 | Yes | 30
6 | 0.92 | 161 | 148.12 | 13.8 | 7.7 | 37.8878 | Yes | 30
7 | 0.86 | 161 | 138.46 | 14.4 | 8.2 | 43.4748 | Yes | 30
8 | 0.88 | 161 | 141.68 | 14.6 | 7.7 | 35.7638 | Yes | 30
9 | 0.87 | 161 | 140.07 | 14.6 | 7.6 | 34.4277 | Yes | 30
10 | 0.87 | 161 | 140.07 | 14.6 | 7.4 | 31.9728 | Yes | 30
11 | 0.87 | 161 | 140.07 | 14.5 | 7.3 | 31.0164 | Yes | 30
12 | 0.82 | 161 | 132.02 | 14.4 | 7.2 | 29.917 | Yes | 30
13 | 0.82 | 161 | 132.02 | 14.4 | 7.2 | 29.917 | Yes | 30
14 | 0.82 | 161 | 132.02 | 14.5 | 8.2 | 42.9929 | Yes | 30
15 | 0.67 | 161 | 107.87 | 15.2 | 8 | 37.4854 | Yes | 30
16 | 0.75 | 161 | 120.75 | 14.7 | 7.7 | 35.0062 | Yes | 30
17 | 0.76 | 161 | 122.36 | 14.6 | 7.3 | 30.4264 | Yes | 30
18 | 0.59 | 161 | 94.99 | 14.5 | 7.2 | 28.9482 | Yes | 30
19 | 0.77 | 161 | 123.97 | 13.6 | 7.3 | 32.5616 | Yes | 30
20 | 0.77 | 161 | 123.97 | 14.4 | 7.4 | 32.0351 | Yes | 30
21 | 0.78 | 161 | 125.58 | 14.7 | 7.5 | 32.6221 | Yes | 30
22 | 0.74 | 161 | 119.14 | 14.5 | 8.2 | 42.6056 | Yes | 30
23 | 0.68 | 161 | 109.48 | 15.2 | 8 | 37.528 | Yes | 30
24 | 0.6 | 161 | 96.6 | 16.1 | 7.2 | 26.038 | Yes | 30
25 | 0.68 | 161 | 109.48 | 14.3 | 7.5 | 33.1241 | Yes | 30
26 | 0.47 | 161 | 75.67 | 16.2 | 7.4 | 27.4507 | Yes | 30
27 | 0.44 | 161 | 70.84 | 14.5 | 7.2 | 28.4567 | Yes | 30
28 | 0.61 | 161 | 98.21 | 14.8 | 7.5 | 31.7844 | Yes | 30
29 | 0.63 | 161 | 101.43 | 14.3 | 7.8 | 36.7969 | Yes | 30
30 | 0.64 | 161 | 103.04 | 14.6 | 8.1 | 40.3354 | Yes | 30
31 | 0.59 | 161 | 94.99 | 15.4 | 7.4 | 29.3587 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: