## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-01-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.16
2 |  |  | 0.16
3 |  |  | 0.14
4 |  |  | 0.07
5 |  |  | 0.06
6 |  |  | 0.6
7 |  |  | 0.06
8 |  |  | 0.06
9 |  |  | 0.05
10 |  |  | 0.06
11 |  |  | 0.05
12 |  |  | 0.06
13 |  |  | 0.06
14 |  |  | 0.05
15 |  |  | 0.05
16 |  |  | 0.05
17 |  |  | 0.05
18 |  |  | 0.05
19 |  |  | 0.06
20 |  |  | 0.05
21 |  |  | 0.06
22 |  |  | 0.05
23 |  |  | 0.06
24 |  |  | 0.05
25 |  |  | 0.05
26 |  |  | 0.05
27 |  |  | 0.05
28 |  |  | 0.19
29 |  |  | 0.05
30 |  |  | 0.06
31 |  |  | 0.05
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-01-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.68 | 161 | 109.48 | 14.6 | 7.5 | 32.4686 | Yes | 30
2 | 0.6 | 161 | 96.6 | 15.4 | 7.3 | 28.3212 | Yes | 30
3 | 0.59 | 161 | 94.99 | 15.4 | 7.8 | 34.0463 | Yes | 30
4 | 0.67 | 161 | 107.87 | 16.1 | 8.2 | 38.0138 | Yes | 30
5 | 0.61 | 161 | 98.21 | 15.6 | 7.8 | 33.6725 | Yes | 30
6 | 0.62 | 161 | 99.82 | 15.3 | 7.5 | 30.777 | Yes | 30
7 | 0.68 | 161 | 109.48 | 14.3 | 7.2 | 29.6404 | Yes | 30
8 | 0.63 | 161 | 101.43 | 14.8 | 7.2 | 28.5033 | Yes | 30
9 | 0.71 | 161 | 114.31 | 14.5 | 7.3 | 30.4561 | Yes | 30
10 | 0.77 | 161 | 123.97 | 14.1 | 7.2 | 30.3487 | Yes | 30
11 | 0.83 | 161 | 133.63 | 14.1 | 7.3 | 31.7102 | Yes | 30
12 | 0.78 | 161 | 125.58 | 14.3 | 8.2 | 43.3695 | Yes | 30
13 | 0.69 | 161 | 111.09 | 14.2 | 7.3 | 31.0012 | Yes | 30
14 | 0.68 | 161 | 109.48 | 14.1 | 7.2 | 30.0389 | Yes | 30
15 | 0.71 | 161 | 114.31 | 14.1 | 7.4 | 32.4597 | Yes | 30
16 | 0.71 | 161 | 114.31 | 14.1 | 7.2 | 30.1418 | Yes | 30
17 | 0.77 | 161 | 123.97 | 13.9 | 7.8 | 38.3922 | Yes | 30
18 | 0.68 | 161 | 109.48 | 13.6 | 7.7 | 37.3634 | Yes | 30
19 | 0.7 | 161 | 112.7 | 13.7 | 7.4 | 33.2983 | Yes | 30
20 | 0.59 | 161 | 94.99 | 13.7 | 7.3 | 31.6894 | Yes | 30
21 | 0.68 | 161 | 109.48 | 12.6 | 7.2 | 33.1988 | Yes | 30
22 | 0.6 | 161 | 96.6 | 12.8 | 7.9 | 42.0302 | Yes | 30
23 | 0.71 | 161 | 114.31 | 12.5 | 7.6 | 38.8711 | Yes | 30
24 | 0.75 | 161 | 120.75 | 13.1 | 7.3 | 33.5878 | Yes | 30
25 | 0.66 | 161 | 106.26 | 13 | 7.5 | 36.0348 | Yes | 30
26 | 0.65 | 161 | 104.65 | 12.6 | 7.6 | 38.3523 | Yes | 30
27 | 0.65 | 161 | 104.65 | 12.6 | 7.4 | 35.624 | Yes | 30
28 | 0.64 | 161 | 103.04 | 12.3 | 7.3 | 35.4411 | Yes | 30
29 | 0.66 | 161 | 106.26 | 11.8 | 7.3 | 36.682 | Yes | 30
30 | 0.6 | 161 | 96.6 | 13 | 8.2 | 46.3144 | Yes | 30
31 | 0.7 | 161 | 112.7 | 12.7 | 8 | 44.394 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: