## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-02-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.05
2 |  |  | 0.06
3 |  |  | 0.06
4 |  |  | 0.06
5 |  |  | 0.06
6 |  |  | 0.06
7 |  |  | 0.06
8 |  |  | 0.06
9 |  |  | 0.06
10 |  |  | 0.06
11 |  |  | 0.06
12 |  |  | 0.06
13 |  |  | 0.06
14 |  |  | 0.06
15 |  |  | 0.06
16 |  |  | 0.06
17 |  |  | 0.06
18 |  |  | 0.08
19 |  |  | 0.08
20 |  |  | 0.11
21 |  |  | 0.11
22 |  |  | 0.11
23 |  |  | 0.09
24 |  |  | 0.09
25 |  |  | 0.1
26 |  |  | 0.2
27 |  |  | 0.25
28 |  |  | 0.15
29 |  |  | 0
30 |  |  | 0
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-02-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.73 | 161 | 117.53 | 13 | 7.6 | 37.6874 | Yes | 30
2 | 0.86 | 161 | 138.46 | 12.8 | 7.5 | 37.355 | Yes | 30
3 | 0.82 | 161 | 132.02 | 13.3 | 7.3 | 33.4083 | Yes | 30
4 | 0.91 | 161 | 146.51 | 13 | 7.5 | 37.0717 | Yes | 30
5 | 0.88 | 161 | 141.68 | 13.4 | 7.4 | 34.6721 | Yes | 30
6 | 0.96 | 161 | 154.56 | 13.6 | 7.5 | 35.8253 | Yes | 30
7 | 1.07 | 161 | 172.27 | 12.7 | 7.6 | 39.9557 | Yes | 30
8 | 1.2 | 161 | 193.2 | 12.6 | 8.2 | 50.8871 | Yes | 30
9 | 0.92 | 161 | 148.12 | 13.4 | 8.2 | 46.7652 | Yes | 30
10 | 1.1 | 161 | 177.1 | 13 | 7.6 | 39.3017 | Yes | 30
11 | 1 | 161 | 161 | 11.7 | 7.3 | 38.3386 | Yes | 30
12 | 0.98 | 161 | 157.78 | 11.9 | 7.2 | 36.4815 | Yes | 30
13 | 0.65 | 161 | 104.65 | 12 | 7.2 | 34.9535 | Yes | 30
14 | 0.67 | 161 | 107.87 | 12.9 | 7.4 | 34.9997 | Yes | 30
15 | 0.68 | 161 | 109.48 | 12.8 | 7.4 | 35.2733 | Yes | 30
16 | 0.63 | 161 | 101.43 | 11.8 | 7.4 | 37.8427 | Yes | 30
17 | 0.46 | 161 | 74.06 | 12.8 | 7.4 | 34.4027 | Yes | 30
18 | 0.39 | 161 | 62.79 | 12.4 | 7.2 | 33.1156 | Yes | 30
19 | 0.38 | 161 | 61.18 | 11.5 | 7.7 | 41.6509 | Yes | 30
20 | 0.49 | 161 | 78.89 | 11.8 | 7.7 | 41.3472 | Yes | 30
21 | 0.5 | 161 | 80.5 | 12.2 | 7.3 | 35.1244 | Yes | 30
22 | 0.62 | 161 | 99.82 | 12.7 | 7.3 | 33.9881 | Yes | 30
23 | 0.61 | 161 | 98.21 | 13.2 | 7.4 | 34.0749 | Yes | 30
24 | 0.62 | 161 | 99.82 | 13.2 | 7.4 | 34.1137 | Yes | 30
25 | 0.5 | 161 | 80.5 | 14.2 | 7.5 | 32.6696 | Yes | 30
26 | 0.35 | 161 | 56.35 | 11.5 | 7.5 | 38.721 | Yes | 30
27 | 0.61 | 161 | 98.21 | 11.7 | 7.7 | 42.1841 | Yes | 30
28 | 0.53 | 161 | 85.33 | 12.3 | 7.6 | 38.8246 | Yes | 30
29 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
30 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: