## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-03-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.085
2 |  |  | 0.08
3 |  |  | 0.068
4 |  |  | 0.063
5 |  |  | 0.063
6 |  |  | 0.063
7 |  |  | 0.065
8 |  |  | 0.068
9 |  |  | 0.067
10 |  |  | 0.069
11 |  |  | 0.067
12 |  |  | 0.069
13 |  |  | 0.072
14 |  |  | 0.072
15 |  |  | 0.074
16 |  |  | 0.074
17 |  |  | 0.072
18 |  |  | 0.071
19 |  |  | 0.07
20 |  |  | 0.069
21 |  |  | 0.071
22 |  |  | 0.077
23 |  |  | 0.105
24 |  |  | 0.098
25 |  |  | 0.086
26 |  |  | 0.075
27 |  |  | 0.065
28 |  |  | 0.064
29 |  |  | 0.062
30 |  |  | 0.067
31 |  |  | 0.065
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-03-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.47 | 161 | 75.67 | 12.5 | 7.4 | 35.1361 | Yes | 30
2 | 0.4 | 161 | 64.4 | 13.6 | 7.4 | 32.3962 | Yes | 30
3 | 0.39 | 161 | 62.79 | 13.2 | 7.2 | 30.8615 | Yes | 30
4 | 0.4 | 161 | 64.4 | 12.6 | 7.7 | 38.6807 | Yes | 30
5 | 0.44 | 161 | 70.84 | 13.1 | 7.4 | 33.646 | Yes | 30
6 | 0.4 | 161 | 64.4 | 12.9 | 7.3 | 32.7098 | Yes | 30
7 | 0.42 | 161 | 67.62 | 13 | 7.2 | 31.383 | Yes | 30
8 | 0.46 | 161 | 74.06 | 13.9 | 7.2 | 29.6885 | Yes | 30
9 | 0.55 | 161 | 88.55 | 13.2 | 7.4 | 33.8433 | Yes | 30
10 | 0.66 | 161 | 106.26 | 13.2 | 8 | 42.7544 | Yes | 30
11 | 0.77 | 161 | 123.97 | 13.2 | 7.4 | 34.7001 | Yes | 30
12 | 0.91 | 161 | 146.51 | 13.9 | 7.2 | 31.2509 | Yes | 30
13 | 0.92 | 161 | 148.12 | 13.8 | 7.3 | 32.6837 | Yes | 30
14 | 0.97 | 161 | 156.17 | 12.5 | 7.3 | 35.8403 | Yes | 30
15 | 0.88 | 161 | 141.68 | 13.3 | 7.4 | 34.9035 | Yes | 30
16 | 0.82 | 161 | 132.02 | 13.1 | 7.3 | 33.8561 | Yes | 30
17 | 0.74 | 161 | 119.14 | 13.3 | 7.2 | 31.903 | Yes | 30
18 | 0.68 | 161 | 109.48 | 12.8 | 8 | 44.0015 | Yes | 30
19 | 0.62 | 161 | 99.82 | 13.6 | 7.6 | 35.7653 | Yes | 30
20 | 0.65 | 161 | 104.65 | 12.8 | 7.4 | 35.1533 | Yes | 30
21 | 0.63 | 161 | 101.43 | 13.6 | 7.3 | 32.047 | Yes | 30
22 | 0.59 | 161 | 94.99 | 13 | 7.4 | 34.4531 | Yes | 30
23 | 0.55 | 161 | 88.55 | 13.7 | 7.3 | 31.5454 | Yes | 30
24 | 0.51 | 161 | 82.11 | 13.6 | 7.2 | 30.4623 | Yes | 30
25 | 0.53 | 161 | 85.33 | 13.7 | 7.9 | 39.2828 | Yes | 30
26 | 0.52 | 161 | 83.72 | 14.6 | 7.8 | 35.6229 | Yes | 30
27 | 0.47 | 161 | 75.67 | 14.4 | 7.4 | 30.9592 | Yes | 30
28 | 0.41 | 161 | 66.01 | 14.3 | 7.3 | 29.8277 | Yes | 30
29 | 0.41 | 161 | 66.01 | 14.2 | 7.3 | 30.0275 | Yes | 30
30 | 0.4 | 161 | 64.4 | 14.2 | 7.4 | 31.1258 | Yes | 30
31 | 0.42 | 161 | 67.62 | 13.5 | 7.2 | 30.3534 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: