## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-05-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.08
2 |  |  | 0.08
3 |  |  | 0.09
4 |  |  | 0.08
5 |  |  | 0.08
6 |  |  | 0.08
7 |  |  | 0.11
8 |  |  | 0.13
9 |  |  | 0.11
10 |  |  | 0.11
11 |  |  | 0.1
12 |  |  | 0.11
13 |  |  | 0.1
14 |  |  | 0.11
15 |  |  | 0.1
16 |  |  | 0.09
17 |  |  | 0.12
18 |  |  | 0.1
19 |  |  | 0.1
20 |  |  | 0.14
21 |  |  | 0.13
22 |  |  | 0.13
23 |  |  | 0.13
24 |  |  | 0.12
25 |  |  | 0.12
26 |  |  | 0.11
27 |  |  | 0.11
28 |  |  | 0.11
29 |  |  | 0.11
30 |  |  | 0.1
31 |  |  | 0.1
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-05-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.75 | 161 | 120.75 | 16 | 7.3 | 27.6772 | Yes | 30
2 | 0.86 | 161 | 138.46 | 14.6 | 7.5 | 33.1404 | Yes | 30
3 | 0.8 | 161 | 128.8 | 15 | 7.4 | 30.884 | Yes | 30
4 | 0.8 | 161 | 128.8 | 15 | 8.2 | 41.498 | Yes | 30
5 | 0.72 | 161 | 115.92 | 15 | 7.2 | 28.4152 | Yes | 30
6 | 0.68 | 161 | 109.48 | 15 | 7.2 | 28.2857 | Yes | 30
7 | 0.66 | 161 | 106.26 | 15 | 7.2 | 28.2211 | Yes | 30
8 | 0.69 | 161 | 111.09 | 15.3 | 7.3 | 28.8056 | Yes | 30
9 | 0.62 | 161 | 99.82 | 15.4 | 7.6 | 31.7261 | Yes | 30
10 | 0.62 | 161 | 99.82 | 15.4 | 8.2 | 39.5964 | Yes | 30
11 | 0.57 | 161 | 91.77 | 15.7 | 7.2 | 26.6537 | Yes | 30
12 | 0.57 | 161 | 91.77 | 15.4 | 7.2 | 27.1946 | Yes | 30
13 | 0.52 | 161 | 83.72 | 15.2 | 7.3 | 28.4415 | Yes | 30
14 | 0.52 | 161 | 83.72 | 15.3 | 7.7 | 32.7675 | Yes | 30
15 | 0.58 | 161 | 93.38 | 15.6 | 7.7 | 32.3391 | Yes | 30
16 | 0.55 | 161 | 88.55 | 15.5 | 7.6 | 31.2651 | Yes | 30
17 | 0.54 | 161 | 86.94 | 15.6 | 8.1 | 37.3199 | Yes | 30
18 | 0.49 | 161 | 78.89 | 15.7 | 8.1 | 36.8631 | Yes | 30
19 | 0.51 | 161 | 82.11 | 15.8 | 7.6 | 30.5062 | Yes | 30
20 | 0.6 | 161 | 96.6 | 14.3 | 7.2 | 29.3711 | Yes | 30
21 | 0.64 | 161 | 103.04 | 15 | 7.4 | 30.3259 | Yes | 30
22 | 0.6 | 161 | 96.6 | 14.9 | 7.4 | 30.3902 | Yes | 30
23 | 0.59 | 161 | 94.99 | 15.3 | 7.4 | 29.5555 | Yes | 30
24 | 0.58 | 161 | 93.38 | 15.9 | 7.6 | 30.546 | Yes | 30
25 | 0.59 | 161 | 94.99 | 15.3 | 7.8 | 34.2737 | Yes | 30
26 | 0.52 | 161 | 83.72 | 15.7 | 7.8 | 33.1085 | Yes | 30
27 | 0.6 | 161 | 96.6 | 15.7 | 7.6 | 31.0269 | Yes | 30
28 | 0.58 | 161 | 93.38 | 15.4 | 7.5 | 30.4333 | Yes | 30
29 | 0.59 | 161 | 94.99 | 15.7 | 7.4 | 28.776 | Yes | 30
30 | 0.62 | 161 | 99.82 | 15.9 | 7.3 | 27.4521 | Yes | 30
31 | 0.5 | 161 | 80.5 | 16 | 7.4 | 27.9161 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: