## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-06-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.17
2 |  |  | 0.16
3 |  |  | 0.16
4 |  |  | 0.16
5 |  |  | 0.16
6 |  |  | 0.16
7 |  |  | 0.17
8 |  |  | 0.18
9 |  |  | 0.16
10 |  |  | 0.15
11 |  |  | 0.2
12 |  |  | 0.1
13 |  |  | 0.19
14 |  |  | 0.18
15 |  |  | 0.18
16 |  |  | 0.19
17 |  |  | 0.2
18 |  |  | 0.25
19 |  |  | 0.32
20 |  |  | 0.29
21 |  |  | 0.27
22 |  |  | 0.26
23 |  |  | 0.26
24 |  |  | 0.25
25 |  |  | 0.49
26 |  |  | 0.63
27 |  |  | 0.64
28 |  |  | 0.62
29 |  |  | 0.65
30 |  |  | 0
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-06-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.64 | 161 | 103.04 | 16.3 | 7.3 | 26.7878 | Yes | 30
2 | 0.66 | 161 | 106.26 | 16.5 | 7.2 | 25.5236 | Yes | 30
3 | 0.74 | 161 | 119.14 | 15.7 | 7.2 | 27.177 | Yes | 30
4 | 0.74 | 161 | 119.14 | 15.9 | 7.5 | 29.976 | Yes | 30
5 | 0.72 | 161 | 115.92 | 15.9 | 7.5 | 29.9077 | Yes | 30
6 | 0.77 | 161 | 123.97 | 16.1 | 7.2 | 26.5495 | Yes | 30
7 | 0.69 | 161 | 111.09 | 16.2 | 7.4 | 28.1495 | Yes | 30
8 | 0.65 | 161 | 104.65 | 16.7 | 7.3 | 26.1092 | Yes | 30
9 | 0.77 | 161 | 123.97 | 16.6 | 7.2 | 25.6745 | Yes | 30
10 | 0.68 | 161 | 109.48 | 16.8 | 7.8 | 31.3335 | Yes | 30
11 | 0.62 | 161 | 99.82 | 16.8 | 7.7 | 29.9877 | Yes | 30
12 | 0.68 | 161 | 109.48 | 16.6 | 7.9 | 32.9514 | Yes | 30
13 | 0.61 | 161 | 98.21 | 16.6 | 7.7 | 30.3562 | Yes | 30
14 | 0.59 | 161 | 94.99 | 17.2 | 7.8 | 30.197 | Yes | 30
15 | 0.57 | 161 | 91.77 | 17.2 | 7.9 | 31.2657 | Yes | 30
16 | 0.54 | 161 | 86.94 | 16.5 | 7.4 | 27.1211 | Yes | 30
17 | 0.58 | 161 | 93.38 | 16.5 | 7.4 | 27.2454 | Yes | 30
18 | 0.41 | 161 | 66.01 | 17.6 | 7.4 | 24.8207 | Yes | 30
19 | 0.51 | 161 | 82.11 | 16.8 | 7.7 | 29.6139 | Yes | 30
20 | 0.53 | 161 | 85.33 | 16.5 | 7.5 | 28.1159 | Yes | 30
21 | 0.56 | 161 | 90.16 | 17 | 7.7 | 29.388 | Yes | 30
22 | 0.7 | 161 | 112.7 | 16.9 | 7.8 | 31.1962 | Yes | 30
23 | 0.71 | 161 | 114.31 | 16.3 | 7.5 | 29.086 | Yes | 30
24 | 0.9 | 161 | 144.9 | 17 | 7.4 | 27.3303 | Yes | 30
25 | 1 | 161 | 161 | 17 | 7.4 | 27.6444 | Yes | 30
26 | 1 | 161 | 161 | 17 | 7.5 | 28.6906 | Yes | 30
27 | 1 | 161 | 161 | 17 | 7.3 | 26.6353 | Yes | 30
28 | 0.91 | 161 | 146.51 | 16.8 | 7.2 | 25.7418 | Yes | 30
29 | 0.81 | 161 | 130.41 | 17.1 | 8.1 | 34.8296 | Yes | 30
30 | 0.78 | 161 | 125.58 | 17.3 | 8 | 33.0089 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: