## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-07-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.66
2 |  |  | 0.66
3 |  |  | 0.68
4 |  |  | 0.68
5 |  |  | 0.68
6 |  |  | 0.68
7 |  |  | 0.68
8 |  |  | 0.69
9 |  |  | 0.67
10 |  |  | 0.68
11 |  |  | 0.67
12 |  |  | 0.64
13 |  |  | 0.65
14 |  |  | 0.66
15 |  |  | 0.66
16 |  |  | 0.64
17 |  |  | 0.65
18 |  |  | 0.64
19 |  |  | 0.64
20 |  |  | 0.6
21 |  |  | 0.6
22 |  |  | 0.58
23 |  |  | 0.59
24 |  |  | 0.63
25 |  |  | 0.66
26 |  |  | 0.68
27 |  |  | 0.67
28 |  |  | 0.65
29 |  |  | 0.58
30 |  |  | 0.67
31 |  |  | 0.69
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
[5 empty] | SIGNATURE: Ron Wanner |  |  | 2025-08-02
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-07-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.77 | 161 | 123.97 | 7.4 | 7.5 | 53.2598 | Yes | 30
2 | 0.64 | 161 | 103.04 | 17.5 | 7.4 | 25.6551 | Yes | 30
3 | 0.6 | 161 | 96.6 | 17 | 7.4 | 26.4084 | Yes | 30
4 | 0.43 | 161 | 69.23 | 17.5 | 7.6 | 26.9815 | Yes | 30
5 | 0.53 | 161 | 85.33 | 17.6 | 7.6 | 27.1096 | Yes | 30
6 | 0.49 | 161 | 78.89 | 17.7 | 7.5 | 25.8264 | Yes | 30
7 | 0.48 | 161 | 77.28 | 17.8 | 7.6 | 26.5964 | Yes | 30
8 | 0.54 | 161 | 86.94 | 17.9 | 7.6 | 26.6008 | Yes | 30
9 | 0.52 | 161 | 83.72 | 18.2 | 8 | 30.1793 | Yes | 30
10 | 0.46 | 161 | 74.06 | 18 | 7.7 | 27.1748 | Yes | 30
11 | 0.51 | 161 | 82.11 | 18.1 | 7.5 | 25.2003 | Yes | 30
12 | 0.46 | 161 | 74.06 | 18.1 | 7.4 | 24.139 | Yes | 30
13 | 0.4 | 161 | 64.4 | 18.5 | 7.4 | 23.3371 | Yes | 30
14 | 0.38 | 161 | 61.18 | 18.9 | 7.5 | 23.5282 | Yes | 30
15 | 0.4 | 161 | 64.4 | 18.5 | 7.4 | 23.3371 | Yes | 30
16 | 0.41 | 161 | 66.01 | 18.7 | 7.5 | 23.929 | Yes | 30
17 | 0.43 | 161 | 69.23 | 19 | 7.8 | 26.287 | Yes | 30
18 | 0.5 | 161 | 80.5 | 19.1 | 8.1 | 29.4255 | Yes | 30
19 | 0.59 | 161 | 94.99 | 18.9 | 7.8 | 26.9526 | Yes | 30
20 | 0.62 | 161 | 99.82 | 19.1 | 7.7 | 25.7102 | Yes | 30
21 | 0.66 | 161 | 106.26 | 18.9 | 7.8 | 27.1692 | Yes | 30
22 | 0.72 | 161 | 115.92 | 18.9 | 7.8 | 27.3562 | Yes | 30
23 | 0.71 | 161 | 114.31 | 19.1 | 7.5 | 24.1103 | Yes | 30
24 | 0.72 | 161 | 115.92 | 19 | 7.3 | 22.5512 | Yes | 30
25 | 0.74 | 161 | 119.14 | 19.1 | 7.5 | 24.1935 | Yes | 30
26 | 0.81 | 161 | 130.41 | 19 | 7.5 | 24.5529 | Yes | 30
27 | 0.82 | 161 | 132.02 | 18.7 | 7.5 | 25.0812 | Yes | 30
28 | 0.9 | 161 | 144.9 | 18.6 | 7.4 | 24.5501 | Yes | 30
29 | 0.87 | 161 | 140.07 | 18.7 | 8 | 30.3767 | Yes | 30
30 | 0.84 | 161 | 135.24 | 19 | 8 | 29.6727 | Yes | 30
31 | 0.85 | 161 | 136.85 | 19.2 | 7.6 | 25.2613 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: