## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-08-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.69
2 |  |  | 0.67
3 |  |  | 0.68
4 |  |  | 0.61
5 |  |  | 0.63
6 |  |  | 0.59
7 |  |  | 0.62
8 |  |  | 0.62
9 |  |  | 0.64
10 |  |  | 0.65
11 |  |  | 0.64
12 |  |  | 0.62
13 |  |  | 0.64
14 |  |  | 0.62
15 |  |  | 0.61
16 |  |  | 0.64
17 |  |  | 0.65
18 |  |  | 0.63
19 |  |  | 0.6
20 |  |  | 0.65
21 |  |  | 0.63
22 |  |  | 0.65
23 |  |  | 0.66
24 |  |  | 0.67
25 |  |  | 0.6
26 |  |  | 0.61
27 |  |  | 0.61
28 |  |  | 0.61
29 |  |  | 0.62
30 |  |  | 0.62
31 |  |  | 0.53
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-08-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.89 | 161 | 143.29 | 19.2 | 7.6 | 25.3773 | Yes | 30
2 | 0.81 | 161 | 130.41 | 19.2 | 7.5 | 24.2252 | Yes | 30
3 | 0.82 | 161 | 132.02 | 19.2 | 7.6 | 25.1746 | Yes | 30
4 | 0.76 | 161 | 122.36 | 19.2 | 7.5 | 24.0866 | Yes | 30
5 | 0.78 | 161 | 125.58 | 18.9 | 7.6 | 25.569 | Yes | 30
6 | 0.78 | 161 | 125.58 | 19.4 | 7.6 | 24.7252 | Yes | 30
7 | 0.8 | 161 | 128.8 | 18.9 | 7.7 | 26.5997 | Yes | 30
8 | 0.61 | 161 | 98.21 | 18.9 | 7.5 | 24.1577 | Yes | 30
9 | 0.83 | 161 | 133.63 | 19.4 | 7.4 | 23.0784 | Yes | 30
10 | 0.8 | 161 | 128.8 | 19.7 | 7.4 | 22.539 | Yes | 30
11 | 0.96 | 161 | 154.56 | 19.7 | 7.2 | 21.3016 | Yes | 30
12 | 1.31 | 161 | 210.91 | 20 | 7.7 | 26.1945 | Yes | 30
13 | 1.27 | 161 | 204.47 | 20.3 | 7.6 | 24.6205 | Yes | 30
14 | 1.12 | 161 | 180.32 | 20 | 7.4 | 22.9162 | Yes | 30
15 | 1.17 | 161 | 188.37 | 19.8 | 8 | 29.2076 | Yes | 30
16 | 0.99 | 161 | 159.39 | 19.8 | 8.1 | 29.6956 | Yes | 30
17 | 0.87 | 161 | 140.07 | 19.9 | 7.7 | 25.0747 | Yes | 30
18 | 0.64 | 161 | 103.04 | 19.5 | 7.5 | 23.2826 | Yes | 30
19 | 0.6 | 161 | 96.6 | 19.5 | 7.4 | 22.3252 | Yes | 30
20 | 0.58 | 161 | 93.38 | 19.3 | 7.5 | 23.4359 | Yes | 30
21 | 0.45 | 161 | 72.45 | 19.6 | 7.5 | 22.6268 | Yes | 30
22 | 0.5 | 161 | 80.5 | 19.3 | 7.4 | 22.3692 | Yes | 30
23 | 0.53 | 161 | 85.33 | 20.5 | 7.4 | 20.701 | Yes | 30
24 | 0.74 | 161 | 119.14 | 20.2 | 7.6 | 23.3236 | Yes | 30
25 | 0.56 | 161 | 90.16 | 20.3 | 8 | 26.3448 | Yes | 30
26 | 0.58 | 161 | 93.38 | 21.3 | 7.5 | 20.4794 | Yes | 30
27 | 0.67 | 161 | 107.87 | 20.9 | 7.3 | 19.7221 | Yes | 30
28 | 0.84 | 161 | 135.24 | 20.3 | 7.8 | 25.2506 | Yes | 30
29 | 0.78 | 161 | 125.58 | 20.4 | 7.8 | 24.9098 | Yes | 30
30 | 0.66 | 161 | 106.26 | 21.1 | 7.6 | 21.7506 | Yes | 30
31 | 0.63 | 161 | 101.43 | 20.8 | 7.6 | 22.1185 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: