## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-09-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.61
2 |  |  | 0.49
3 |  |  | 0.65
4 |  |  | 0.67
5 |  |  | 0.64
6 |  |  | 0.6
7 |  |  | 0.64
8 |  |  | 0.6
9 |  |  | 0.61
10 |  |  | 0.65
11 |  |  | 0.68
12 |  |  | 0.68
13 |  |  | 0.69
14 |  |  | 0.62
15 |  |  | 0.59
16 |  |  | 0.59
17 |  |  | 0.6
18 |  |  | 0.67
19 |  |  | 0.48
20 |  |  | 0.43
21 |  |  | 0.42
22 |  |  | 0.59
23 |  |  | 0.41
24 |  |  | 0.61
25 |  |  | 0.47
26 |  |  | 0.67
27 |  |  | 0.63
28 |  |  | 0.52
29 |  |  | 0.51
30 |  |  | 0.52
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-09-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.69 | 161 | 111.09 | 20.5 | 7.4 | 21.0865 | Yes | 30
2 | 0.63 | 161 | 101.43 | 20.4 | 7.3 | 20.3066 | Yes | 30
3 | 0.62 | 161 | 99.82 | 21.2 | 7.9 | 24.0583 | Yes | 30
4 | 0.42 | 161 | 67.62 | 21.5 | 7.7 | 21.3805 | Yes | 30
5 | 0.58 | 161 | 93.38 | 21.3 | 7.5 | 20.4794 | Yes | 30
6 | 0.62 | 161 | 99.82 | 20.6 | 7.4 | 20.7762 | Yes | 30
7 | 0.71 | 161 | 114.31 | 20.4 | 7.5 | 22.0906 | Yes | 30
8 | 0.74 | 161 | 119.14 | 20.4 | 7.3 | 20.5661 | Yes | 30
9 | 0.75 | 161 | 120.75 | 20.3 | 7.6 | 23.1938 | Yes | 30
10 | 0.75 | 161 | 120.75 | 20.2 | 7.4 | 21.6671 | Yes | 30
11 | 0.7 | 161 | 112.7 | 20.5 | 8.2 | 28.4526 | Yes | 30
12 | 0.75 | 161 | 120.75 | 19.9 | 7.7 | 24.7321 | Yes | 30
13 | 0.8 | 161 | 128.8 | 19.4 | 7.5 | 23.8744 | Yes | 30
14 | 0.75 | 161 | 120.75 | 19.7 | 8 | 28.0269 | Yes | 30
15 | 0.72 | 161 | 115.92 | 19.7 | 8 | 27.931 | Yes | 30
16 | 0.55 | 161 | 88.55 | 20.3 | 7.4 | 21.031 | Yes | 30
17 | 0.69 | 161 | 111.09 | 19.7 | 7.5 | 23.1037 | Yes | 30
18 | 0.8 | 161 | 128.8 | 18.9 | 7.4 | 23.7857 | Yes | 30
19 | 0.8 | 161 | 128.8 | 18.9 | 7.6 | 25.6276 | Yes | 30
20 | 0.68 | 161 | 109.48 | 19 | 7.6 | 25.1086 | Yes | 30
21 | 0.58 | 161 | 93.38 | 19.1 | 7.6 | 24.6564 | Yes | 30
22 | 0.69 | 161 | 111.09 | 18.7 | 7.4 | 23.8051 | Yes | 30
23 | 0.68 | 161 | 109.48 | 18.8 | 7.6 | 25.4479 | Yes | 30
24 | 0.67 | 161 | 107.87 | 18.6 | 7.7 | 26.739 | Yes | 30
25 | 0.61 | 161 | 98.21 | 18.7 | 7.5 | 24.4845 | Yes | 30
26 | 0.82 | 161 | 132.02 | 17.9 | 7.6 | 27.4663 | Yes | 30
27 | 0.86 | 161 | 138.46 | 18.1 | 7.5 | 26.231 | Yes | 30
28 | 0.64 | 161 | 103.04 | 18.3 | 7.5 | 25.2376 | Yes | 30
29 | 0.77 | 161 | 123.97 | 18.4 | 7.6 | 26.4103 | Yes | 30
30 | 0.8 | 161 | 128.8 | 17.8 | 7.4 | 25.6091 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: