## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-10-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.52
2 |  |  | 0.55
3 |  |  | 0.6
4 |  |  | 0.62
5 |  |  | 0.66
6 |  |  | 0.6
7 |  |  | 0.62
8 |  |  | 0.62
9 |  |  | 0.61
10 |  |  | 0.6
11 |  |  | 0.57
12 |  |  | 0.67
13 |  |  | 0.64
14 |  |  | 0.62
15 |  |  | 0.61
16 |  |  | 0.41
17 |  |  | 0.48
18 |  |  | 0.63
19 |  |  | 0.61
20 |  |  | 0.47
21 |  |  | 0.52
22 |  |  | 0.51
23 |  |  | 0.59
24 |  |  | 0.61
25 |  |  | 0.59
26 |  |  | 0.63
27 |  |  | 0.62
28 |  |  | 0.61
29 |  |  | 0.59
30 |  |  | 0.56
31 |  |  | 0.51
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-10-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.78 | 161 | 125.58 | 17.9 | 7.5 | 26.3426 | Yes | 30
2 | 0.75 | 161 | 120.75 | 17.3 | 7.5 | 27.3289 | Yes | 30
3 | 0.7 | 161 | 112.7 | 17.6 | 7.5 | 26.6326 | Yes | 30
4 | 0.68 | 161 | 109.48 | 18.1 | 7.3 | 23.8492 | Yes | 30
5 | 0.69 | 161 | 111.09 | 17.5 | 7.5 | 26.7809 | Yes | 30
6 | 0.71 | 161 | 114.31 | 17.3 | 7.3 | 25.2524 | Yes | 30
7 | 0.78 | 161 | 125.58 | 17 | 7.6 | 29.0373 | Yes | 30
8 | 0.71 | 161 | 114.31 | 16.6 | 7.5 | 28.5086 | Yes | 30
9 | 0.69 | 161 | 111.09 | 16.3 | 7.4 | 27.9618 | Yes | 30
10 | 0.74 | 161 | 119.14 | 16.7 | 7.7 | 30.6043 | Yes | 30
11 | 0.77 | 161 | 123.97 | 17.2 | 7.7 | 29.701 | Yes | 30
12 | 0.64 | 161 | 103.04 | 17.2 | 7.7 | 29.2638 | Yes | 30
13 | 0.71 | 161 | 114.31 | 16.7 | 7.6 | 29.3895 | Yes | 30
14 | 0.78 | 161 | 125.58 | 14.8 | 7.6 | 33.6267 | Yes | 30
15 | 0.8 | 161 | 128.8 | 15.9 | 7.5 | 30.1818 | Yes | 30
16 | 0.94 | 161 | 151.34 | 15.9 | 7.5 | 30.6673 | Yes | 30
17 | 0.67 | 161 | 107.87 | 17.2 | 7.6 | 28.2941 | Yes | 30
18 | 0.68 | 161 | 109.48 | 15.9 | 7.6 | 30.896 | Yes | 30
19 | 0.63 | 161 | 101.43 | 16.6 | 7.5 | 28.2493 | Yes | 30
20 | 0.73 | 161 | 117.53 | 16.4 | 7.4 | 27.9026 | Yes | 30
21 | 0.94 | 161 | 151.34 | 15.9 | 7.9 | 35.5581 | Yes | 30
22 | 0.95 | 161 | 152.95 | 16.2 | 7.5 | 30.0936 | Yes | 30
23 | 0.92 | 161 | 148.12 | 16 | 7.8 | 33.9638 | Yes | 30
24 | 0.87 | 161 | 140.07 | 16.3 | 7.6 | 30.7407 | Yes | 30
25 | 0.61 | 161 | 98.21 | 16.9 | 7.9 | 32.043 | Yes | 30
26 | 0.77 | 161 | 123.97 | 16.2 | 7.5 | 29.4821 | Yes | 30
27 | 0.75 | 161 | 120.75 | 16.2 | 7.4 | 28.343 | Yes | 30
28 | 0.75 | 161 | 120.75 | 15.4 | 7.6 | 32.1991 | Yes | 30
29 | 0.61 | 161 | 98.21 | 15.4 | 7.4 | 29.4258 | Yes | 30
30 | 0.76 | 161 | 122.36 | 15.2 | 7.5 | 31.481 | Yes | 30
31 | 0.59 | 161 | 94.99 | 15.7 | 7.3 | 27.7268 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: