## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-11-25
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.6
2 |  |  | 0.62
3 |  |  | 0.64
4 |  |  | 0.57
5 |  |  | 0.41
6 |  |  | 0.49
7 |  |  | 0.63
8 |  |  | 0.64
9 |  |  | 0.57
10 |  |  | 0.42
11 |  |  | 0.35
12 |  |  | 0.46
13 |  |  | 0.51
14 |  |  | 0.65
15 |  |  | 0.64
16 |  |  | 0.62
17 |  |  | 0.65
18 |  |  | 0.67
19 |  |  | 0.64
20 |  |  | 0.67
21 |  |  | 0.68
22 |  |  | 0.65
23 |  |  | 0.38
24 |  |  | 0.63
25 |  |  | 0.66
26 |  |  | 0.7
27 |  |  | 0.72
28 |  |  | 0.41
29 |  |  | 0.39
30 |  |  | 0.37
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-11-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.59 | 161 | 94.99 | 15.6 | 7.2 | 26.8943 | Yes | 30
2 | 0.53 | 161 | 85.33 | 15.5 | 7.2 | 26.8899 | Yes | 30
3 | 0.47 | 161 | 75.67 | 15.9 | 7.4 | 28.0073 | Yes | 30
4 | 0.39 | 161 | 62.79 | 15.4 | 7.2 | 26.6405 | Yes | 30
5 | 0.37 | 161 | 59.57 | 15 | 7.2 | 27.3013 | Yes | 30
6 | 0.53 | 161 | 85.33 | 15.6 | 7.2 | 26.7104 | Yes | 30
7 | 0.81 | 161 | 130.41 | 16.2 | 7.2 | 26.4932 | Yes | 30
8 | 0.94 | 161 | 151.34 | 16 | 7.2 | 27.2527 | Yes | 30
9 | 0.81 | 161 | 130.41 | 16.2 | 7.8 | 33.0979 | Yes | 30
10 | 0.84 | 161 | 135.24 | 15.5 | 7.9 | 36.1041 | Yes | 30
11 | 0.64 | 161 | 103.04 | 15.9 | 7.7 | 31.9161 | Yes | 30
12 | 0.66 | 161 | 106.26 | 15.6 | 7.6 | 31.4488 | Yes | 30
13 | 0.65 | 161 | 104.65 | 15 | 7.4 | 30.3605 | Yes | 30
14 | 0.68 | 161 | 109.48 | 15.4 | 7.2 | 27.5388 | Yes | 30
15 | 0.66 | 161 | 106.26 | 15.9 | 7.2 | 26.5712 | Yes | 30
16 | 0.7 | 161 | 112.7 | 15.3 | 7.3 | 28.8385 | Yes | 30
17 | 0.68 | 161 | 109.48 | 15.3 | 7.2 | 27.7237 | Yes | 30
18 | 0.68 | 161 | 109.48 | 15.1 | 7.7 | 33.8166 | Yes | 30
19 | 0.71 | 161 | 114.31 | 15.1 | 7.6 | 32.7001 | Yes | 30
20 | 0.72 | 161 | 115.92 | 14.9 | 7.5 | 31.9711 | Yes | 30
21 | 0.8 | 161 | 128.8 | 15.2 | 7.3 | 29.3651 | Yes | 30
22 | 0.92 | 161 | 148.12 | 14.7 | 7.2 | 29.6599 | Yes | 30
23 | 0.89 | 161 | 143.29 | 15.5 | 7.2 | 28.0194 | Yes | 30
24 | 1.06 | 161 | 170.66 | 13.6 | 7.2 | 32.4314 | Yes | 30
25 | 1.08 | 161 | 173.88 | 14.9 | 7.3 | 30.9309 | Yes | 30
26 | 0.93 | 161 | 149.73 | 14.8 | 7.2 | 29.4961 | Yes | 30
27 | 0.89 | 161 | 143.29 | 14.6 | 7.2 | 29.7566 | Yes | 30
28 | 0.81 | 161 | 130.41 | 14.7 | 7.2 | 29.29 | Yes | 30
29 | 0.72 | 161 | 115.92 | 14.5 | 7.3 | 30.4908 | Yes | 30
30 | 0.72 | 161 | 115.92 | 14.2 | 7.2 | 29.9754 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: