## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-12-01
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.32
2 |  |  | 0.28
3 |  |  | 0.23
4 |  |  | 0.23
5 |  |  | 0.22
6 |  |  | 0.24
7 |  |  | 0.23
8 |  |  | 0.27
9 |  |  | 0.3
10 |  |  | 0.6
11 |  |  | 0.67
12 |  |  | 0.64
13 |  |  | 0.52
14 |  |  | 0.37
15 |  |  | 0.37
16 |  |  | 0.31
17 |  |  | 0.54
18 |  |  | 0.62
19 |  |  | 0.37
20 |  |  | 0.65
21 |  |  | 0.62
22 |  |  | 0.55
23 |  |  | 0.33
24 |  |  | 0.23
25 |  |  | 0.2
26 |  |  | 0.18
27 |  |  | 0.17
28 |  |  | 0.16
29 |  |  | 0.15
30 |  |  | 0.14
31 |  |  | 0.22
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
[5 empty] | SIGNATURE: Ron Wanner |  |  | 2026-01-03
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 161 | 101.43 | 14.5 | 7.2 | 29.0806 | Yes | 30
2 | 0.61 | 161 | 98.21 | 15 | 7.6 | 32.5463 | Yes | 30
3 | 0.65 | 161 | 104.65 | 14.2 | 7.7 | 35.781 | Yes | 30
4 | 0.65 | 161 | 104.65 | 14.5 | 7.6 | 33.8017 | Yes | 30
5 | 0.65 | 161 | 104.65 | 14.1 | 7.5 | 33.4539 | Yes | 30
6 | 0.62 | 161 | 99.82 | 14.8 | 7.9 | 36.8907 | Yes | 30
7 | 0.62 | 161 | 99.82 | 15.4 | 7.9 | 35.4484 | Yes | 30
8 | 0.62 | 161 | 99.82 | 14.5 | 7.8 | 36.2699 | Yes | 30
9 | 0.61 | 161 | 98.21 | 14.6 | 7.7 | 34.6838 | Yes | 30
10 | 0.59 | 161 | 94.99 | 14.9 | 7.6 | 32.6894 | Yes | 30
11 | 0.55 | 161 | 88.55 | 14.9 | 7.6 | 32.5409 | Yes | 30
12 | 0.45 | 161 | 72.45 | 16.1 | 7.8 | 31.9819 | Yes | 30
13 | 0.39 | 161 | 62.79 | 15.1 | 7.9 | 35.2304 | Yes | 30
14 | 0.3 | 161 | 48.3 | 14.8 | 7.8 | 34.2845 | Yes | 30
15 | 0.34 | 161 | 54.74 | 14.9 | 7.6 | 31.7724 | Yes | 30
16 | 0.4 | 161 | 64.4 | 15.1 | 7.5 | 30.4183 | Yes | 30
17 | 0.53 | 161 | 85.33 | 14.8 | 7.4 | 30.3506 | Yes | 30
18 | 0.75 | 161 | 120.75 | 14.2 | 7.3 | 31.2138 | Yes | 30
19 | 0.89 | 161 | 143.29 | 14.7 | 7.5 | 33.0329 | Yes | 30
20 | 0.98 | 161 | 157.78 | 14.1 | 7.5 | 34.7324 | Yes | 30
21 | 0.98 | 161 | 157.78 | 14.9 | 7.5 | 32.9312 | Yes | 30
22 | 0.9 | 161 | 144.9 | 14.9 | 7.5 | 32.6328 | Yes | 30
23 | 0.9 | 161 | 144.9 | 14.4 | 7.5 | 33.7378 | Yes | 30
24 | 0.81 | 161 | 130.41 | 14.9 | 7.5 | 32.3003 | Yes | 30
25 | 0.72 | 161 | 115.92 | 14.3 | 7.5 | 33.2751 | Yes | 30
26 | 0.7 | 161 | 112.7 | 14.1 | 7.3 | 31.2442 | Yes | 30
27 | 0.61 | 161 | 98.21 | 14 | 7.6 | 34.7869 | Yes | 30
28 | 0.56 | 161 | 90.16 | 14.8 | 7.5 | 31.604 | Yes | 30
29 | 0.56 | 161 | 90.16 | 14 | 7.5 | 33.3345 | Yes | 30
30 | 0.61 | 161 | 98.21 | 13.4 | 7.4 | 33.6243 | Yes | 30
31 | 0.66 | 161 | 106.26 | 14 | 7.3 | 31.3103 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: