## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-01-26
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.13
2 |  |  | 0.13
3 |  |  | 0.14
4 |  |  | 0.13
5 |  |  | 0.12
6 |  |  | 0.12
7 |  |  | 0.12
8 |  |  | 0.22
9 |  |  | 0.26
10 |  |  | 0.33
11 |  |  | 0.26
12 |  |  | 0.18
13 |  |  | 0.13
14 |  |  | 0.1
15 |  |  | 0.1
16 |  |  | 0.1
17 |  |  | 0.11
18 |  |  | 0.11
19 |  |  | 0.1
20 |  |  | 0.1
21 |  |  | 0.09
22 |  |  | 0.09
23 |  |  | 0.09
24 |  |  | 0.09
25 |  |  | 0.1
26 |  |  | 0.09
27 |  |  | 0.09
28 |  |  | 0.09
29 |  |  | 0.09
30 |  |  | 0.09
31 |  |  | 0.18
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2026-01-26 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.58 | 161 | 93.38 | 14 | 7.3 | 31.0263 | Yes | 30
2 | 0.63 | 161 | 101.43 | 14.2 | 7.2 | 29.6693 | Yes | 30
3 | 0.72 | 161 | 115.92 | 13.5 | 7.5 | 35.0947 | Yes | 30
4 | 0.69 | 161 | 111.09 | 13.8 | 7.5 | 34.2842 | Yes | 30
5 | 0.72 | 161 | 115.92 | 13.4 | 7.4 | 34.0474 | Yes | 30
6 | 0.72 | 161 | 115.92 | 13.1 | 7.4 | 34.7339 | Yes | 30
7 | 0.72 | 161 | 115.92 | 13.1 | 7.4 | 34.7339 | Yes | 30
8 | 0.67 | 161 | 107.87 | 12.7 | 7.4 | 35.4684 | Yes | 30
9 | 0.74 | 161 | 119.14 | 14.1 | 7.7 | 36.3895 | Yes | 30
10 | 0.75 | 161 | 120.75 | 13.6 | 7.7 | 37.6612 | Yes | 30
11 | 0.74 | 161 | 119.14 | 13.3 | 7.6 | 36.9858 | Yes | 30
12 | 0.76 | 161 | 122.36 | 13.3 | 7.6 | 37.0698 | Yes | 30
13 | 0.75 | 161 | 120.75 | 13.3 | 7.5 | 35.686 | Yes | 30
14 | 0.69 | 161 | 111.09 | 14 | 7.5 | 33.8308 | Yes | 30
15 | 0.74 | 161 | 119.14 | 13.3 | 7.6 | 36.9858 | Yes | 30
16 | 0.73 | 161 | 117.53 | 13.4 | 7.6 | 36.6992 | Yes | 30
17 | 0.79 | 161 | 127.19 | 13.4 | 7.5 | 35.6109 | Yes | 30
18 | 0.79 | 161 | 127.19 | 124 | 7.4 | -0.7897 | Yes | 30
19 | 0.77 | 161 | 123.97 | 13.9 | 7.4 | 33.1203 | Yes | 30
20 | 0.72 | 161 | 115.92 | 12.8 | 7.4 | 35.4339 | Yes | 30
21 | 0.74 | 161 | 119.14 | 13.4 | 7.7 | 38.1215 | Yes | 30
22 | 0.72 | 161 | 115.92 | 13.2 | 7.7 | 38.5435 | Yes | 30
23 | 0.76 | 161 | 122.36 | 12.4 | 7.6 | 39.5745 | Yes | 30
24 | 0.77 | 161 | 123.97 | 12.4 | 7.6 | 39.6187 | Yes | 30
25 | 0.77 | 161 | 123.97 | 12 | 7.6 | 40.667 | Yes | 30
26 | 0.78 | 161 | 125.58 | 12 | 7.6 | 40.7126 | Yes | 30
27 | 0.81 | 161 | 130.41 | 11.6 | 8 | 48.281 | Yes | 30
28 | 0.79 | 161 | 127.19 | 12 | 7.9 | 45.2788 | Yes | 30
29 | 0.67 | 161 | 107.87 | 12.5 | 7.7 | 40.1477 | Yes | 30
30 | 0.77 | 161 | 123.97 | 12.3 | 7.6 | 39.8779 | Yes | 30
31 | 0.82 | 161 | 132.02 | 12.3 | 7.4 | 37.417 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: