## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-02-26
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.77
2 |  |  | 0.79
3 |  |  | 0.81
4 |  |  | 0.09
5 |  |  | 0.09
6 |  |  | 0.08
7 |  |  | 0.08
8 |  |  | 0.1
9 |  |  | 0.08
10 |  |  | 0.07
11 |  |  | 0.08
12 |  |  | 0.08
13 |  |  | 0.07
14 |  |  | 0.08
15 |  |  | 0.08
16 |  |  | 0.08
17 |  |  | 0.083
18 |  |  | 0.08
19 |  |  | 0.08
20 |  |  | 0.07
21 |  |  | 0.08
22 |  |  | 0.08
23 |  |  | 0.07
24 |  |  | 0.08
25 |  |  | 0.08
26 |  |  | 0.08
27 |  |  | 0.08
28 |  |  | 0.08
29 |  |  | 0
30 |  |  | 0
31 |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2026-02-26 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.83 | 161 | 133.63 | 13 | 7.5 | 36.7368 | Yes | 30
2 | 0.8 | 161 | 128.8 | 12.6 | 7.3 | 34.9221 | Yes | 30
3 | 0.73 | 161 | 117.53 | 14.2 | 7.4 | 32.3175 | Yes | 30
4 | 0.73 | 161 | 117.53 | 11.9 | 7.3 | 36.7291 | Yes | 30
5 | 0.82 | 161 | 132.02 | 12 | 8.3 | 52.3685 | Yes | 30
6 | 0.85 | 161 | 136.85 | 12.4 | 7.8 | 42.8656 | Yes | 30
7 | 0.83 | 161 | 133.63 | 12.7 | 7.5 | 37.4762 | Yes | 30
8 | 0.89 | 161 | 143.29 | 12.9 | 7.4 | 35.8851 | Yes | 30
9 | 0.88 | 161 | 141.68 | 12.7 | 7.3 | 35.0072 | Yes | 30
10 | 0.86 | 161 | 138.46 | 12.7 | 7.3 | 34.9278 | Yes | 30
11 | 0.6 | 161 | 96.6 | 12.9 | 7.4 | 34.7225 | Yes | 30
12 | 0.85 | 161 | 136.85 | 12.5 | 7.9 | 44.1033 | Yes | 30
13 | 0.88 | 161 | 141.68 | 13 | 7.9 | 42.8119 | Yes | 30
14 | 0.86 | 161 | 138.46 | 13 | 7.7 | 39.683 | Yes | 30
15 | 0.82 | 161 | 132.02 | 12.9 | 7.6 | 38.3276 | Yes | 30
16 | 0.78 | 161 | 125.58 | 13.4 | 7.5 | 35.5705 | Yes | 30
17 | 0.75 | 161 | 120.75 | 13.7 | 7.4 | 33.4881 | Yes | 30
18 | 0.79 | 161 | 127.19 | 12.5 | 7.4 | 36.436 | Yes | 30
19 | 0.7 | 161 | 112.7 | 12.3 | 7.8 | 42.4258 | Yes | 30
20 | 0.63 | 161 | 101.43 | 11.9 | 7.7 | 41.7277 | Yes | 30
21 | 0.66 | 161 | 106.26 | 12.5 | 7.6 | 38.6515 | Yes | 30
22 | 0.61 | 161 | 98.21 | 12.9 | 7.6 | 37.4257 | Yes | 30
23 | 0.58 | 161 | 93.38 | 13.1 | 7.5 | 35.4723 | Yes | 30
24 | 0.58 | 161 | 93.38 | 12.5 | 7.5 | 36.9156 | Yes | 30
25 | 0.58 | 161 | 93.38 | 12.6 | 7.5 | 36.6711 | Yes | 30
26 | 0.59 | 161 | 94.99 | 12.3 | 7.4 | 36.4767 | Yes | 30
27 | 0.69 | 161 | 111.09 | 12.6 | 7.7 | 39.9728 | Yes | 30
28 | 0.74 | 161 | 119.14 | 13.4 | 7.7 | 38.1215 | Yes | 30
29 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
30 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
31 | 0 | 161 | 0 |  |  | 8.3699 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: