## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Clatsop
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-03-26
System Name: | Jewell SD#8 |  |  | ID#: 41 | 90531 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.08
2 |  |  | 0.07
3 |  |  | 0.08
4 |  |  | 0.07
5 |  |  | 0.08
6 |  |  | 0.08
7 |  |  | 0.09
8 |  |  | 0.09
9 |  |  | 0.09
10 |  |  | 0.08
11 |  |  | 0.08
12 |  |  | 0.08
13 |  |  | 0.11
14 |  |  | 0.24
15 |  |  | 0.27
16 |  |  | 0.28
17 |  |  | 0.2
18 |  |  | 0.12
19 |  |  | 0.09
20 |  |  | 0.08
21 |  |  | 0.08
22 |  |  | 0.08
23 |  |  | 0.08
24 |  |  | 0.08
25 |  |  | 0.08
26 |  |  | 0.2
27 |  |  | 0.22
28 |  |  | 0.13
29 |  |  | 0.1
30 |  |  | 0.09
31 |  |  | 0.09
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Ronald Wanner
SIGNATURE: Ron Wanner
[5 empty] | 503-741-6362 |  |  | t-08898 D-08782
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Jewell SD#8
System Name: | Jewell SD#8 |  | ID#: 41 | 90531 | Month/Year: | 2026-03-26 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.78 | 161 | 125.58 | 12.3 | 7.7 | 41.338 | Yes | 30
2 | 0.86 | 161 | 138.46 | 12.7 | 7.6 | 39.0163 | Yes | 30
3 | 0.82 | 161 | 132.02 | 13.3 | 7.5 | 35.9707 | Yes | 30
4 | 0.9 | 161 | 144.9 | 12.9 | 7.5 | 37.2765 | Yes | 30
5 | 0.86 | 161 | 138.46 | 13 | 7.4 | 35.5261 | Yes | 30
6 | 0.86 | 161 | 138.46 | 12.4 | 7.6 | 40.019 | Yes | 30
7 | 0.85 | 161 | 136.85 | 13.9 | 7.7 | 37.3394 | Yes | 30
8 | 0.87 | 161 | 140.07 | 14 | 7.7 | 37.1764 | Yes | 30
9 | 0.81 | 161 | 130.41 | 13.9 | 7.6 | 35.8235 | Yes | 30
10 | 0.82 | 161 | 132.02 | 13.9 | 7.5 | 34.5636 | Yes | 30
11 | 0.85 | 161 | 136.85 | 13 | 7.5 | 36.8202 | Yes | 30
12 | 0.79 | 161 | 127.19 | 13.1 | 7.5 | 36.3282 | Yes | 30
13 | 0.8 | 161 | 128.8 | 13.1 | 7.5 | 36.3694 | Yes | 30
14 | 0.87 | 161 | 140.07 | 12.9 | 7.8 | 41.4925 | Yes | 30
15 | 0.8 | 161 | 128.8 | 13 | 7.9 | 42.4262 | Yes | 30
16 | 0.79 | 161 | 127.19 | 13.2 | 7.9 | 41.8204 | Yes | 30
17 | 0.81 | 161 | 130.41 | 13 | 7.8 | 40.9393 | Yes | 30
18 | 0.68 | 161 | 109.48 | 14.8 | 7.8 | 35.7968 | Yes | 30
19 | 0.64 | 161 | 103.04 | 15 | 7.7 | 33.888 | Yes | 30
20 | 0.65 | 161 | 104.65 | 14.4 | 7.6 | 34.0275 | Yes | 30
21 | 0.55 | 161 | 88.55 | 14.2 | 8 | 39.5169 | Yes | 30
22 | 0.57 | 161 | 91.77 | 13.4 | 7.8 | 38.7982 | Yes | 30
23 | 0.57 | 161 | 91.77 | 14.2 | 7.7 | 35.4575 | Yes | 30
24 | 0.57 | 161 | 91.77 | 13.9 | 7.5 | 33.5953 | Yes | 30
25 | 0.56 | 161 | 90.16 | 13.9 | 7.5 | 33.5572 | Yes | 30
26 | 0.61 | 161 | 98.21 | 13.4 | 7.4 | 33.6243 | Yes | 30
27 | 0.6 | 161 | 96.6 | 13.3 | 7.4 | 33.8104 | Yes | 30
28 | 0.63 | 161 | 101.43 | 13.6 | 7.3 | 32.047 | Yes | 30
29 | 0.7 | 161 | 112.7 | 13.5 | 7.3 | 32.5193 | Yes | 30
30 | 0.68 | 161 | 109.48 | 13.6 | 7.3 | 32.2299 | Yes | 30
31 | 0.69 | 161 | 111.09 | 13.5 | 7.7 | 37.6551 | Yes | 30
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2
Note on I5: Ron: