## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Galice Resort |  |  | ID#: 41-90808 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 48 | 48 | 0 | 25 | 0.069 | 0.07
2 | 46 | 46 | 0 | 25 | 0.08 | 0.08
3 | 46 | 46 | 0 | 25 | 0.08 | 0.08
4 | 46 | 46 | 0 | 25 | 0.07 | 0.07
5 | 41 | 41 | 0 | 25 | 0.07 | 0.07
6 | 41 | 41 | 0 | 25 | 0.07 | 0.07
7 | 41 | 41 | 0 | 25 | 0.07 | 0.07
8 | 47 | 47 | 0 | 25 | 0.109 | 0.11
9 | 47 | 47 | 0 | 25 | 0.085 | 0.09
10 | 48 | 48 | 0 | 25 | 0.08 | 0.08
11 | 40 | 40 | 0 | 25 | 0.07 | 0.07
12 | 61 | 61 | 0 | 25 | 0.1 | 0.1
13 | 46 | 46 | 0 | 25 | 0.07 | 0.07
14 | 47 | 47 | 0 | 25 | 0.07 | 0.07
15 | 61 | 61 | 0 | 25 | 0.08 | 0.08
16 | 48 | 48 | 0 | 25 | 0.07 | 0.07
17 | 48 | 48 | 0 | 25 | 0.07 | 0.07
18 | 46 | 46 | 0 | 25 | 0.08 | 0.08
19 | 43 | 43 | 0 | 25 | 0.07 | 0.07
20 | 48 | 48 | 0 | 25 | 0.07 | 0.07
21 | 47 | 47 | 0 | 25 | 0.1 | 0.1
22 | 49 | 49 | 0 | 25 | 0.129 | 0.13
23 | 47 | 47 | 0 | 25 | 0.08 | 0.08
24 | 44 | 44 | 0 | 25 | 0.07 | 0.07
25 | 44 | 44 | 0 | 25 | 0.08 | 0.08
26 | 39 | 39 | 0 | 25 | 0.08 | 0.08
27 | 50 | 50 | 0 | 25 | 0.08 | 0.08
28 | 44 | 44 | 0 | 25 | 0.07 | 0.07
29 | 30 | 30 | 0 | 25 | 0.06 | 0.06
30 | 39 | 39 | 0 | 25 | 0.07 | 0.07
31 | 46 | 46 | 0 | 25 | 0.07 | 0.07
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Kurt Swanson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Kurt Swanson
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-476-3818 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | GALICE RESORT |  | 41-90808 |  |  |  | Disinfection Giardia Log Inactiv: | 0.5
341 Gallons /GPM =(T)
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 114 | 91.2 | 36.5 | 8.1 | 4.6368 | YES | 3
2 | 0.8 | 114 | 91.2 | 35.4 | 8.1 | 5.0107 | YES | 3
3 | 0.8 | 114 | 91.2 | 36.9 | 8.2 | 4.688 | YES | 3
4 | 0.8 | 114 | 91.2 | 35.5 | 8.1 | 4.9756 | YES | 3
5 | 0.8 | 114 | 91.2 | 40.6 | 8.2 | 3.5986 | YES | 3
6 | 0.8 | 114 | 91.2 | 40.4 | 8.7 | 4.454 | YES | 3
7 | 0.8 | 114 | 91.2 | 40.4 | 8.6 | 4.2816 | YES | 3
8 | 0.8 | 114 | 91.2 | 40.6 | 8.2 | 3.5986 | YES | 3
9 | 0.8 | 114 | 91.2 | 40.3 | 8.3 | 3.8277 | YES | 3
10 | 0.8 | 114 | 91.2 | 41.8 | 8.1 | 3.1666 | YES | 3
11 | 0.6 | 114 | 68.4 | 42.5 | 8.5 | 3.4515 | YES | 3
12 | 0.8 | 114 | 91.2 | 32.9 | 8.5 | 6.9572 | YES | 3
13 | 0.8 | 114 | 91.2 | 33.8 | 8.2 | 5.8256 | YES | 3
14 | 0.8 | 114 | 91.2 | 33.8 | 8.1 | 5.6046 | YES | 3
15 | 0.8 | 114 | 91.2 | 33.9 | 8.2 | 5.7852 | YES | 3
16 | 0.8 | 114 | 91.2 | 33.8 | 8.3 | 6.0548 | YES | 3
17 | 0.8 | 114 | 91.2 | 33.7 | 8.2 | 5.8663 | YES | 3
18 | 0.8 | 114 | 91.2 | 32.7 | 8.1 | 6.0503 | YES | 3
19 | 0.6 | 114 | 68.4 | 32.4 | 8.4 | 6.7696 | YES | 3
20 | 0.6 | 114 | 68.4 | 31 | 8.1 | 6.6465 | YES | 3
21 | 0.6 | 114 | 68.4 | 31.9 | 8.6 | 7.5618 | YES | 3
22 | 0.6 | 114 | 68.4 | 32.7 | 8.5 | 6.8897 | YES | 3
23 | 0.6 | 114 | 68.4 | 31.4 | 8.1 | 6.4654 | YES | 3
24 | 0.6 | 114 | 68.4 | 32.9 | 8.2 | 6.0561 | YES | 3
25 | 0.4 | 114 | 45.6 | 31.8 | 8.5 | 7.1595 | YES | 3
26 | 0.4 | 114 | 45.6 | 31.9 | 8.3 | 6.5867 | YES | 3
27 | 0.6 | 114 | 68.4 | 33.9 | 8.4 | 6.1028 | YES | 3
28 | 0.6 | 114 | 68.4 | 32.6 | 8.6 | 7.2073 | YES | 3
29 | 0.6 | 114 | 68.4 | 32 | 8.5 | 7.2294 | YES | 3
30 | 0.6 | 114 | 68.4 | 32.5 | 8.6 | 7.257 | YES | 3
31 | 0.6 | 114 | 68.4 | 32.8 | 8.5 | 6.8424 | YES | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2