## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-09-25
System Name: | Galice Resort |  |  | ID#: 41-90808 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 58 | 58 | 0 | 25 | 0.08 | 0.08
2 | 60 | 60 | 0 | 25 | 0.1 | 0.1
3 | 44 | 44 | 0 | 25 | 0.07 | 0.07
4 | 50 | 50 | 0 | 25 | 0.07 | 0.07
5 | 42 | 42 | 0 | 25 | 0.07 | 0.07
6 | 61 | 61 | 0 | 25 | 0.1 | 0.1
7 | 61 | 61 | 0 | 25 | 0.07 | 0.07
8 | 56 | 56 | 0 | 25 | 0.18 | 0.18
9 | 60 | 60 | 0 | 25 | 0.07 | 0.07
10 | 41 | 41 | 0 | 25 | 0.07 | 0.07
11 | 61 | 61 | 0 | 25 | 0.07 | 0.07
12 | 46 | 46 | 0 | 25 | 0.08 | 0.08
13 | 45 | 45 | 0 | 25 | 0.09 | 0.09
14 | 62 | 62 | 0 | 25 | 0.08 | 0.08
15 | 45 | 45 | 0 | 25 | 0.08 | 0.08
16 | 44 | 44 | 0 | 25 | 0.11 | 0.11
17 | 62 | 62 | 0 | 25 | 0.12 | 0.12
18 | 62 | 62 | 0 | 25 | 0.13 | 0.13
19 | 62 | 62 | 0 | 25 | 0.09 | 0.09
20 | 62 | 62 | 0 | 25 | 0.09 | 0.09
21 | 61 | 61 | 0 | 25 | 0.11 | 0.11
22 | 44 | 44 | 0 | 25 | 0.1 | 0.1
23 | 62 | 62 | 0 | 25 | 0.11 | 0.11
24 | 63 | 63 | 0 | 25 | 0.11 | 0.11
25 | 51 | 51 | 0 | 25 | 0.11 | 0.11
26 | 45 | 45 | 0 | 25 | 0.1 | 0.1
27 | 61 | 61 | 0 | 25 | 0.11 | 0.11
28 | 62 | 62 | 0 | 25 | 0.15 | 0.15
29 | 63 | 63 | 0 | 25 | 0.14 | 0.14
30 | 42 | 42 | 0 | 25 | 0.08 | 0.08
31 |  |  |  | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Kurt Swanson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Kurt Swanson
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-476-3818 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | GALICE RESORT |  | 41-90808 |  |  |  | Disinfection Giardia Log Inactiv: | 0.5
341 Gallons /GPM =(T)
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 114 | 68.4 | 33.2 | 8.6 | 6.916 | YES | 3
2 | 0.6 | 114 | 68.4 | 33.2 | 8.6 | 6.916 | YES | 3
3 | 0.6 | 114 | 68.4 | 33.3 | 8.5 | 6.6106 | YES | 3
4 | 0.6 | 114 | 68.4 | 33.6 | 8.4 | 6.231 | YES | 3
5 | 0.4 | 114 | 45.6 | 33.9 | 8.4 | 5.9598 | YES | 3
6 | 0.4 | 114 | 45.6 | 33.9 | 8.5 | 6.1939 | YES | 3
7 | 0.6 | 114 | 68.4 | 33.9 | 8.6 | 6.5902 | YES | 3
8 | 0.6 | 114 | 68.4 | 33.6 | 8.5 | 6.475 | YES | 3
9 | 0.4 | 114 | 45.6 | 33.6 | 8.5 | 6.3239 | YES | 3
10 | 0.4 | 114 | 45.6 | 33.3 | 8.4 | 6.2131 | YES | 3
11 | 0.4 | 114 | 45.6 | 33.3 | 8.6 | 6.7088 | YES | 3
12 | 0.4 | 114 | 45.6 | 33.3 | 8.4 | 6.2131 | YES | 3
13 | 0.6 | 114 | 68.4 | 32.9 | 8.3 | 6.2937 | YES | 3
14 | 0.6 | 114 | 68.4 | 32.9 | 8.4 | 6.54 | YES | 3
15 | 0.6 | 114 | 68.4 | 32.4 | 8.6 | 7.307 | YES | 3
16 | 0.6 | 114 | 68.4 | 32.6 | 8.5 | 6.9373 | YES | 3
17 | 0.6 | 114 | 68.4 | 32.2 | 8.5 | 7.1308 | YES | 3
18 | 0.6 | 114 | 68.4 | 32.5 | 8.4 | 6.7231 | YES | 3
19 | 0.6 | 114 | 68.4 | 32.9 | 8.6 | 7.0603 | YES | 3
20 | 0.6 | 114 | 68.4 | 34.6 | 8.6 | 6.279 | YES | 3
21 | 0.6 | 114 | 68.4 | 33.8 | 8.4 | 6.1452 | YES | 3
22 | 0.6 | 114 | 68.4 | 34.6 | 8.4 | 5.8132 | YES | 3
23 | 0.6 | 114 | 68.4 | 34.3 | 8.6 | 6.4106 | YES | 3
24 | 0.6 | 114 | 68.4 | 34 | 8.6 | 6.5449 | YES | 3
25 | 0.6 | 114 | 68.4 | 34 | 8.6 | 6.5449 | YES | 3
26 | 0.6 | 114 | 68.4 | 34.2 | 8.6 | 6.4551 | YES | 3
27 | 0.6 | 114 | 68.4 | 34.2 | 8.6 | 6.4551 | YES | 3
28 | 0.6 | 114 | 68.4 | 34.2 | 8.6 | 6.4551 | YES | 3
29 | 0.6 | 114 | 68.4 | 34.8 | 8.6 | 6.1926 | YES | 3
30 | 0.4 | 114 | 45.6 | 34.5 | 8.6 | 6.1748 | YES | 3
31 |  | 114 | [5 empty] | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2