## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-01-01
System Name: | Galice Resort |  |  | ID#: 41-90808 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 60 | 60 | 0 | 25 | 0.15 | 0.15
2 | 48 | 48 | 0 | 25 | 0.15 | 0.15
3 | 48 | 48 | 0 | 25 | 0.18 | 0.18
4 | 60 | 60 | 0 | 25 | 0.72 | 0.72
5 |  |  |  | 25 | Offline/Repairs
6 |  |  |  | 25 | Offline/Repairs
7 |  |  |  | 25 | Offline/Repairs
8 | 48 | 48 | 0 | 25 | 0.4 | 0.4
9 | 33 | 33 | 0 | 25 | 0.23 | 0.23
10 | 59 | 59 | 0 | 25 | 0.16 | 0.16
11 | 45 | 45 | 0 | 25 | 0.13 | 0.13
12 | 59 | 59 | 0 | 25 | 0.12 | 0.12
13 | 58 | 58 | 0 | 25 | 0.1 | 0.1
14 | 40 | 40 | 0 | 25 | 0.09 | 0.09
15 | 58 | 58 | 0 | 25 | 0.09 | 0.09
16 | 45 | 45 | 0 | 25 | 0.08 | 0.08
17 | 54 | 54 | 0 | 25 | 0.08 | 0.08
18 | 53 | 53 | 0 | 25 | 0.07 | 0.07
19 | 43 | 43 | 0 | 25 | 0.07 | 0.07
20 | 43 | 43 | 0 | 25 | 0.08 | 0.08
21 | 44 | 44 | 0 | 25 | 0.07 | 0.07
22 | 58 | 58 | 0 | 25 | 0.06 | 0.06
23 | 57 | 57 | 0 | 25 | 0.06 | 0.06
24 | 40 | 40 | 0 | 25 | 0.06 | 0.06
25 | 35 | 35 | 0 | 25 | 0.08 | 0.08
26 | 45 | 45 | 0 | 25 | 0.06 | 0.06
27 | 44 | 44 | 0 | 25 | 0.13 | 0.13
28 | 37 | 37 | 0 | 25 | 0.08 | 0.08
29 | 41 | 41 | 0 | 25 | 0.08 | 0.08
30 | 45 | 45 | 0 | 25 | 0.08 | 0.08
31 | 45 | 45 | 0 | 25 | 0.08 | 0.08
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Kurt Swanson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Kurt Swanson
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-476-3818 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | GALICE RESORT |  | 41-90808 |  |  |  | Disinfection Giardia Log Inactiv: | 0.5
341 Gallons /GPM =(T)
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 114 | 91.2 | 45.4 | 8.1 | 2.4208 | YES | 3
2 | 0.8 | 114 | 91.2 | 44.8 | 8.1 | 2.5333 | YES | 3
3 | 0.8 | 114 | 91.2 | 44.8 | 8.1 | 2.5333 | YES | 3
4 | 0.6 | 114 | 68.4 | 45 | 7.8 | 2.1401 | YES | 3
5 |  | 114 | [5 empty] | 3
6 |  | 114 | [5 empty] | 3
7 |  | 114 | [5 empty] | 3
8 | 0.6 | 114 | 68.4 | 44.5 | 8.5 | 2.981 | YES | 3
9 | 0.4 | 114 | 45.6 | 45 | 8.2 | 2.4713 | YES | 3
10 | 0.4 | 114 | 45.6 | 44 | 8.3 | 2.7776 | YES | 3
11 | 0.6 | 114 | 68.4 | 45.7 | 8.3 | 2.5084 | YES | 3
12 | 0.6 | 114 | 68.4 | 41.7 | 8.4 | 3.5134 | YES | 3
13 | 0.8 | 114 | 91.2 | 41.2 | 8.3 | 3.587 | YES | 3
14 | 0.8 | 114 | 91.2 | 44.1 | 8.1 | 2.6702 | YES | 3
15 | 0.8 | 114 | 91.2 | 40.5 | 8.3 | 3.773 | YES | 3
16 | 0.8 | 114 | 91.2 | 42.6 | 8.3 | 3.2395 | YES | 3
17 | 0.8 | 114 | 91.2 | 40.3 | 8.3 | 3.8277 | YES | 3
18 | 0.8 | 114 | 91.2 | 40.5 | 8.4 | 3.9267 | YES | 3
19 | 0.8 | 114 | 91.2 | 41.9 | 8.3 | 3.4093 | YES | 3
20 | 0.8 | 114 | 91.2 | 41.2 | 8.1 | 3.3087 | YES | 3
21 | 0.8 | 114 | 91.2 | 41.7 | 8.3 | 3.4593 | YES | 3
22 | 0.8 | 114 | 91.2 | 40.1 | 8.4 | 4.0409 | YES | 3
23 | 1.2 | 114 | 136.8 | 43 | 8.2 | 3.1755 | YES | 3
24 | 1.2 | 114 | 136.8 | 42 | 8.3 | 3.5568 | YES | 3
25 | 1.2 | 114 | 136.8 | 41.4 | 8.3 | 3.7145 | YES | 3
26 | 1 | 114 | 114 | 39.6 | 8.3 | 4.1244 | YES | 3
27 | 1.2 | 114 | 136.8 | 41.2 | 8.3 | 3.7684 | YES | 3
28 | 1 | 114 | 114 | 42.8 | 8.3 | 3.2732 | YES | 3
29 | 1.2 | 114 | 136.8 | 42.8 | 8.3 | 3.3559 | YES | 3
30 | 1.2 | 114 | 136.8 | 43 | 8.3 | 3.3072 | YES | 3
31 | 1.2 | 114 | 136.8 | 43.2 | 8.3 | 3.2593 | YES | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. |  |  |  |  | 8.3 |  | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2