## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Josephine
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-26
System Name: | Galice Resort |  |  | ID#: 41-90808 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 45 | 45 | 0 | 25 | 0.07 | 0.07
2 | 40 | 40 | 0 | 25 | 0.07 | 0.07
3 | 43 | 43 | 0 | 25 | 0.08 | 0.08
4 | 44 | 44 | 0 | 25 | 0.08 | 0.08
5 | 26 | 26 | 0 | 25 | 0.06 | 0.06
6 | 30 | 30 | 0 | 25 | 0.06 | 0.06
7 |  |  |  | 25 |  | offline/maintenance
8 |  |  |  | 25 |  | offline/maintenance
9 |  |  |  | 25 |  | offline/maintenance
10 | 45 | 45 | 0 | 25 | 0.26
11 | 42 | 42 | 0 | 25 | 0.13
12 | 40 | 40 | 0 | 25 | 0.16
13 | 35 | 35 | 0 | 25 | 0.21
14 | 35 | 30 | 5 | 25 | 0.2
15 | 34 | 34 | 0 | 25 | 0.13
16 | 31 | 31 | 0 | 25 | 0.09
17 | 37 | 37 | 0 | 25 | 0.11
18 | 40 | 40 | 0 | 25 | 0.16
19 | 40 | 40 | 0 | 25 | 0.25
20 | 40 | 40 | 0 | 25 | 0.16
21 | 35 | 35 | 0 | 25 | 0.1
22 | 31 | 31 | 0 | 25 | 0.1
23 | 42 | 42 | 0 | 25 | 0.85
24 |  |  |  | 25 |  | maintenance/offline
25 |  |  |  | 25 |  | maintenance/offline
26 |  |  |  | 25 |  | maintenance/offline
27 |  |  |  | 25 |  | maintenance/offline
28 | 81 | 80 | 1 | 25 | 0.2 | 0.2
29 |  |  |  | 25
30 |  |  |  | 25
31 |  |  |  | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Kurt Swanson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Kurt Swanson
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-476-3818 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Galice Resort |  | 41-90808 |  |  |  | Disinfection Giardia Log Inactiv: | 0.5
341 Gallons /GPM =(T)
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 114 | 136.8 | 44 | 8.3 | 3.0734 | YES | 3
2 | 1.2 | 114 | 136.8 | 43.2 | 8.3 | 3.2593 | YES | 3
3 | 1.2 | 114 | 136.8 | 43.1 | 8.3 | 3.2832 | YES | 3
4 | 1.4 | 114 | 159.6 | 43.7 | 8.4 | 3.3551 | YES | 3
5 | 1.2 | 114 | 136.8 | 44.4 | 8.3 | 2.9841 | YES | 3
6 | 1.2 | 114 | 136.8 | 44.3 | 8.3 | 3.0062 | YES | 3
7 |  | 114 |  | maintenance | offline |  |  | 3
8 |  | 114 |  | maintenance | offfline |  |  | 3
9 |  | 114 |  | maintenance | offline |  |  | 3
10 | 1.2 | 114 | 136.8 | 46.2 | 8.2 | 2.5025 | YES | 3
11 | 1.2 | 114 | 136.8 | 45.7 | 8.2 | 2.5987 | YES | 3
12 | 0.8 | 114 | 91.2 | 45.8 | 8.2 | 2.4495 | YES | 3
13 | 1 | 114 | 114 | 46.6 | 8.3 | 2.4675 | YES | 3
14 | 1.6 | 114 | 182.4 | 46.8 | 8.2 | 2.5183 | YES | 3
15 | 1 | 114 | 114 | 46.7 | 8.3 | 2.4489 | YES | 3
16 | 1 | 114 | 114 | 46.8 | 8.4 | 2.5347 | YES | 3
17 | 0.8 | 114 | 91.2 | 42.8 | 8.3 | 3.1924 | YES | 3
18 | 0.6 | 114 | 68.4 | 43.7 | 8.3 | 2.9133 | YES | 3
19 | 0.6 | 114 | 68.4 | 44.4 | 8.3 | 2.7655 | YES | 3
20 | 0.6 | 114 | 68.4 | 44 | 8.4 | 2.9688 | YES | 3
21 | 0.6 | 114 | 68.4 | 44.4 | 8.4 | 2.8822 | YES | 3
22 | 0.6 | 114 | 68.4 | 45.7 | 8.3 | 2.5084 | YES | 3
23 | 0.6 | 114 | 68.4 | 45.9 | 8.3 | 2.4707 | YES | 3
24 |  | 114 |  | maintenance | offline |  |  | 3
25 |  | 114 |  | maintenance | offline |  |  | 3
26 |  | 114 |  | maintenance | offline |  |  | 3
27 |  | 114 |  | maintenance | offline |  |  | 3
28 | 2.2 | 114 | 250.8 | 48.9 | 8.2 | 2.3207 | YES | 3
29 |  | 114 | [5 empty] | 3
30 |  | 114 | [5 empty] | 3
31 |  | 114 | [5 empty] | 3
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2