## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | COOS
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-02-21
System Name: | Camp Myrtlewood |  |  | ID#: 41 | 90861 |  | WTP : TP - | SSF/Chlorination
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
OFF
2 |  |  | 0.37 |  |  |  | 0.37
OFF
OFF
OFF
OFF
7 |  |  | 0.26 |  |  |  | 0.26
OFF
OFF
OFF
OFF
12 |  |  | 0.4 |  |  |  | 0.4
13 |  |  | 0.38 |  |  |  | 0.38
OFF
OFF
OFF
OFF
18 |  |  | 0.24 |  |  |  | 0.24
OFF
OFF
OFF
OFF
23 |  |  | 0.22 |  |  |  | 0.22
OFF
OFF
OFF
OFF
28 |  |  | 0.2 |  |  |  | 0.2
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Morgan Woods
[5 empty] | SIGNATURE: Morgan Woods |  |  | DATE: 03/10/2021
[5 empty] | PHONE #: (541)572.5307 |  |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | SSF/Chlorination
System Name: | Camp Myrtlewood |  | ID#: 41 | 90861 | Month/Year: | 2021-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
OFF
2 | 0.4 | 197 | 78.8 | 9.1 | 6.93 | 37.3596 | YES | 2
OFF
OFF
OFF
OFF
7 | 0.4 | 197 | 78.8 | 9.3 | 6.98 | 37.5207 | YES | 2
OFF
OFF
OFF
OFF
12 | 0.4 | 197 | 78.8 | 9.5 | 6.9 | 36.0332 | YES | 2
13 | 0.8 | 197 | 157.6 | 9.4 | 6.91 | 38.0395 | YES | 2
OFF
OFF
OFF
OFF
18 | 0.4 | 197 | 78.8 | 9.9 | 7 | 36.3431 | YES | 2
OFF
OFF
OFF
OFF
23 | 0.4 | 197 | 78.8 | 9.3 | 6.98 | 37.5207 | YES | 2
OFF
OFF
OFF
OFF
28 | 0.4 | 197 | 78.8 | 9 | 6.88 | 36.9596 | YES | 2
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2