## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | COOS
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-06-01
System Name: | Camp Myrtlewood |  |  | ID#: 41 | 90861 |  | WTP : TP - | SSF/Chlorination
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.1
2 |  |  | 0.1
3 |  |  | 0.2
4 |  |  | 0.1
5 |  |  | 0.1
6 |  |  | 0.1
7 |  |  | 0.1
8 |  |  | 0.1
9 |  |  | 0.1
10 |  |  | 0.1
11 |  |  | 0.1
12 |  |  | 0.1
13 |  |  | 0.2
14 |  |  | 0.1
15 |  |  | 0.1
16 |  |  | 0.1
17 |  |  | 0.1
18 |  |  | 0.1
19 |  |  | 0.1
20 |  |  | 0.1
21 |  |  | 0.1
22 |  |  | 0.1
23 |  |  | 0.1
24 |  |  | 0.1
25 |  |  | 0.1
26 |  |  | 0.1
27 |  |  | 0.1
28 |  |  | 0.1
29 |  |  | 0.1
30 |  |  | 0.1
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Reid Hirt
[5 empty] | SIGNATURE: Reid Hirt |  |  | DATE: 07/3/2023
[5 empty] | PHONE #: (541)572.5307 |  |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | SSF/Chlorination
System Name: | Camp Myrtlewood |  | ID#: 41 | 90861 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 43 | 43 | 15.4 | 7.87 | 36.6033 | YES | 0.18
2 | 1 | 43 | 43 | 13.6 | 7.83 | 40.6448 | YES | 0.14
3 | 1 | 43 | 43 | 17.4 | 7.88 | 32.1605 | YES | 0.11
4 | 1 | 43 | 43 | 15.5 | 7.86 | 36.2269 | YES | 0.16
5 | 1 | 43 | 43 | 14.9 | 7.92 | 38.5435 | YES | 0.13
6 | 1 | 43 | 43 | 16.7 | 7.85 | 33.3239 | YES | 0.15
7 | 1 | 43 | 43 | 16.3 | 7.82 | 33.8457 | YES | 0.09
8 | 1 | 43 | 43 | 17.1 | 7.8 | 31.8527 | YES | 0.18
9 | 1 | 43 | 43 | 17.4 | 7.82 | 31.4539 | YES | 0.29
10 | 1 | 43 | 43 | 15.9 | 7.84 | 35.0165 | YES | 0.09
11 | 1 | 43 | 43 | 17.1 | 7.81 | 31.9708 | YES | 0.07
12 | 1 | 43 | 43 | 16.9 | 7.75 | 31.6881 | YES | 0.04
13 | 1 | 43 | 43 | 18.4 | 7.84 | 29.6422 | YES | 0.09
14 | 1 | 43 | 43 | 18 | 7.75 | 29.4452 | YES | 0.02
15 | 1 | 43 | 43 | 15.5 | 7.86 | 36.2269 | YES | 0.11
16 | 1 | 43 | 43 | 16.7 | 7.79 | 32.5924 | YES | 0.06
17 | 1 | 43 | 43 | 18.8 | 7.79 | 28.3296 | YES | 0.04
18 | 1 | 43 | 43 | 17.4 | 7.81 | 31.3376 | YES | 0.04
19 | 1 | 43 | 43 | 16.8 | 7.76 | 32.0184 | YES | 0.02
20 | 1 | 43 | 43 | 17.5 | 7.71 | 29.9967 | YES | 0.04
21 | 1 | 43 | 43 | 15.1 | 7.77 | 35.9873 | YES | 0.02
22 | 1 | 43 | 43 | 17.7 | 7.77 | 30.2647 | YES | 0.04
23 | 1 | 43 | 43 | 19 | 7.77 | 27.7462 | YES | 0.09
24 | 1 | 43 | 43 | 18.5 | 7.78 | 28.7965 | YES | 0.11
25 | 1 | 43 | 43 | 17.7 | 7.85 | 31.1754 | YES | 0.14
26 | 1 | 43 | 43 | 16.5 | 7.88 | 34.1472 | YES | 0.13
27 | 1 | 43 | 43 | 18.8 | 7.75 | 27.9118 | YES | 0.03
28 | 1 | 43 | 43 | 19.6 | 7.79 | 26.8528 | YES | 0.03
29 | 1 | 43 | 43 | 18 | 7.9 | 31.129 | YES | 0.02
30 | 1 | 43 | 43 | 19 | 7.82 | 28.2665 | YES | 0.03
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2