## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | COOS
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-07-01
System Name: | Camp Myrtlewood |  |  | ID#: 41 | 90861 |  | WTP : TP - | SSF/Chlorination
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.1
2 |  |  | 0.1
3 |  |  | 0.3
4 |  |  | 0.1
5 |  |  | 0.25
6 |  |  | 0.1
7 |  |  | 0.1
8 |  |  | 0.1
9 |  |  | 0.1
10 |  |  | 0.2
11 |  |  | 0.4
12 |  |  | 0.1
13 |  |  | 0.1
14 |  |  | 0.1
15 |  |  | 0.1
16 |  |  | 0.1
17 |  |  | 0.3
18 |  |  | 0.3
19 |  |  | 0.1
20 |  |  | 0.1
21 |  |  | 0.2
22 |  |  | 0.1
23 |  |  | 0.1
24 |  |  | 0.09
25 |  |  | 0.1
26 |  |  | 0.1
27 |  |  | 0.1
28 |  |  | 0.1
29 |  |  | 0.3
30 |  |  | 0.1
31 |  |  | 0.2
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Reid Hirt
[5 empty] | SIGNATURE: Reid Hirt |  |  | DATE: 07/31 /2023
[5 empty] | PHONE #: (541)572.5307 |  |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | SSF/Chlorination
System Name: | Camp Myrtlewood |  | ID#: 41 | 90861 | Month/Year: | 2023-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 43 | 43 | 17.3 | 7.85 | 32.018 | YES | 0.04
2 | 1 | 43 | 43 | 16.8 | 7.9 | 33.7205 | YES | 0.06
3 | 1 | 43 | 43 | 16.2 | 7.92 | 35.3542 | YES | 0.1
4 | 1 | 43 | 43 | 17.4 | 7.9 | 32.3995 | YES | 0.02
5 | 1 | 43 | 43 | 18.2 | 7.82 | 29.8188 | YES | 0.15
6 | 1 | 43 | 43 | 19.1 | 7.76 | 27.4589 | YES | 0.19
7 | 1 | 43 | 43 | 18.9 | 7.82 | 28.4561 | YES | 0.18
8 | 1 | 43 | 43 | 18.2 | 7.87 | 30.3767 | YES | 0.13
9 | 1 | 43 | 43 | 17.3 | 7.91 | 32.737 | YES | 0.15
10 | 1 | 43 | 43 | 17.7 | 7.76 | 30.1527 | YES | 0.1
11 | 1 | 43 | 43 | 17.4 | 7.76 | 30.7625 | YES | 0.15
12 | 1 | 43 | 43 | 17.8 | 7.84 | 30.8536 | YES | 0.14
13 | 1 | 43 | 43 | 18.2 | 7.77 | 29.2708 | YES | 0.14
14 | 1 | 43 | 43 | 19.4 | 7.78 | 27.1138 | YES | 0.11
15 | 1 | 43 | 43 | 17.5 | 7.78 | 30.7852 | YES | 0.05
16 | 1 | 43 | 43 | 17.9 | 7.81 | 30.3094 | YES | 0.05
17 | 1 | 43 | 43 | 18.1 | 7.76 | 29.3578 | YES | 0.05
18 | 1 | 43 | 43 | 17.2 | 7.9 | 32.8341 | YES | 0.04
19 | 1 | 43 | 43 | 18.2 | 7.9 | 30.7164 | YES | 0.09
20 | 1 | 43 | 43 | 19 | 7.87 | 28.7962 | YES | 0.13
21 | 1 | 43 | 43 | 18.9 | 7.85 | 28.7749 | YES | 0.14
22 | 1 | 43 | 43 | 17 | 7.86 | 32.7857 | YES | 0.15
23 | 1 | 43 | 43 | 18.7 | 8.05 | 31.4065 | YES | 0.15
24 | 1 | 43 | 43 | 18.9 | 7.91 | 29.4228 | YES | 0.09
25 | 1 | 43 | 43 | 19.9 | 7.87 | 27.1135 | YES | 0.02
26 | 1 | 43 | 43 | 17 | 7.81 | 32.1846 | YES | 0.03
27 | 1 | 43 | 43 | 19.2 | 7.79 | 27.5816 | YES | 0.05
28 | 1 | 43 | 43 | 19 | 7.91 | 29.2269 | YES | 0.04
29 | 1 | 43 | 43 | 17.8 | 8.01 | 32.858 | YES | 0.06
30 | 1 | 43 | 43 | 16.2 | 7.88 | 34.8357 | YES | 0.09
31 | 1 | 43 | 43 | 17.7 | 7.92 | 31.9941 | YES | 0.06
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2